## Sheet1
Link | Title | Images | Application | Standard | Max. Permissible Ambient Temperature | Tensile Load | Shrinkage Test | Shore-Hardness | Pressure Test at High Temperature | Mineral Oil Resistance | Acid and Alkaline Resistance | Ammonia Resistance | Weather Resistance | Conductor | Insulation | Core Identification | Sheath | Cable Construction | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | Moulded 3 Pin Cords | Moulded Two Pin Plug | Part Number | Item | No. of Cores and Nominal Cross Sectional (Sq. mm) | Current Rating (A) | Length | Primary Braid | Secondary Braid | Max. Operating Voltage | Table I : Current Ratings for Multiple Circuits | ('Part Number', 'Part Number') | ('Cable Size', 'Cable Size') | ('Conductor', 'Nom.Cross Sectional Area (Sq. mm)') | ('Conductor', 'No. & Dia.of Wiresin (mm)') | ('Conductor', 'Max. Conductor Diameter (mm)') | ('Conductor', 'Min. Conductor Diameter (mm)') | ('Radial Thickness', 'Min. PVC Insulation') | ('Nylon Braidand Lacquer', 'Max.(mm)') | ('Nylon Braidand Lacquer', 'Min.(mm)') | ('Overall Diameter of Cable', 'Max.(mm)') | ('Overall Diameter of Cable', 'Min.(mm)') | ('DC Conductor Resistance at 20°C (Ω/km)', 'DC Conductor Resistance at 20°C (Ω/km)') | ('Max. Current Rating (Amps.) – BS G 177', 'Max. Current Rating (Amps.) – BS G 177') | ('Nominal Cross Sectional Area (Sq. mm)', 'Nominal Cross Sectional Area (Sq. mm)') | ('Max. Current Rating (Amps)', 'Single Cable') | ('Max. Current Rating (Amps)', '3 – Bunched Cables') | ('Max. Current Rating (Amps)', '7 – Bunched Cables') | ('Max. Current Rating (Amps)', '12 – Bunched Cables') | Voltage Rating: | Test Voltage | Temperature Range | Properties | Nominal Cross-Sectional Area (Sq. mm) | Max. Strand Diameter (mm) | Max. DC Conductor Resistance (Ω/km) | Nominal Insulation Thickness (mm) | Nominal Cable Diameter (mm) | ('Nominal Cross Sectional Area of Conductor (Sq. mm)', 'Nominal Cross Sectional Area of Conductor (Sq. mm)') | ('Current Rating at a Maximum Duty Cycle of', '100% A') | ('Current Rating at a Maximum Duty Cycle of', '85% A') | ('Current Rating at a Maximum Duty Cycle of', '60% A') | ('Current Rating at a Maximum Duty Cycle of', '30% A') | ('Current Rating at a Maximum Duty Cycle of', '20% A') | Voltage Rating | Total Radial Thickness of Covering (mm) | Maximum Cable Diameter (mm) | Approx. Weight (kg/km) | Cable Design Parameters | Overall Dimensions (mm) | Permissible Current Rating (A)** | Voltage Drop (ΔU) at cos Φ = 0.8 (V/A x km) | Material | No. of Wires | Strand Diameter (mm) | Width (mm) | Thickness (mm) | Description | ('Nominal Cross-Sectional Area (Sq. mm)', 'Nominal Cross-Sectional Area (Sq. mm)') | ('Conductor Details', 'No. of Strand') | ('Conductor Details', 'Max. DC Conductor Resistance at 20°C (?/Km)') | ('Approx. Conductor Diameter (mm)', 'Approx. Conductor Diameter (mm)') | ('Approx Net Weight (kg/km)', 'Approx Net Weight (kg/km)') | Flexible Braided Copper & Tin Copper tapes accordingly DIN 72333 Part 3 Standard |  | Technical Data | Nominal Cross Sectional Area (Sq. mm)
https://www.rrkabel.com/application-based-cables/solar-cable | SOLAR CABLE | ['https://www.rrkabel.com/Uploads/Products/128/ProductZoomForMoreDetailsImage/02.jpg', 'https://www.rrkabel.com/Uploads/Products/128/ProductZoomImage/03.jpg', 'https://www.rrkabel.com/Uploads/Products/382/ProductFeaturesDetails/01.png', 'https://www.rrkabel.com/Uploads/Products/382/ProductFeaturesDetails/01.png'] | ['Solar cables are intented for use in photovoltaic power supply systems and similar applications as free hanging, movable, fixed installation and buried in ground in constructional covered systems. The cables can be used indoor, outdoor, in hazard explosion areas, in industry and agriculture. They are suitable for applications in equipment with protective insulation (protecting Class 2).'] | ['EN 50618:2015.'] | ['+90°C (stationary and in motion )'] | ['15 N / mm² in operation. 50 N/mm² during installation'] | ['According to EN 60811 - 1 - 3'] | ['85 shore A according to DIN EN 53505'] | ['According to EN 60811 - 3 - 1'] | ['24h, 100°C according to DIN VDE 0473 - 811 - 2 - 1, DIN EN 60811-2-1'] | ['According to EN 60811-2-1', '7 days, 23°C (N-Oxalic Acid, N-Sodium Hydroxide)'] | ['30 days in saturated ammonia atmosphere (internal testing)'] | ['Ozone resistance according to DIN EN 50396 test Type B, HD 22.2 test Type B UV - resistance according to UL 1581', '(Xenon - Test), ISO 4892 - 2 (Method A) and HD 506/A1-2.4.20', 'Absorption of water (gravimetric) according to DIN VDE 0473-811-1-3, DIN EN 60811 - 1 - 3.'] | ['Fine Wire Tinned Copper Conductor according to BS EN 60228:2005 cl. 5.'] | ['UV resistant, cross linkable, halogen free, flame retardant compound for core insulation.'] | ['Red, black or natural'] | ['UV resistant, cross linkable, halogen free, flame retardant compound for Sheath over insulation.'] | ['Please complete the part numbers for these cables by adding the suffix (in place of "xx") for the insulation colour required as per the list: 02 - black, 03 - red, 13 - natural.']
[19 empty] | Part Number | Nominal Cross-Sectional (Sq. mm) | Insulation Thickness (mm) | Outer sheath Thickness (mm) | Approx. Cable Diameter (mm) as per EN 50618 | Current carrying capacity according to method of installation | Current carrying capacity according to method of installation | Current carrying capacity according to method of installation | Max. Conductor Resistance at 20°C, (Ω/Km)
[19 empty] | Part Number | Nominal Cross-Sectional (Sq. mm) | EN 50618 (Nominal) | EN 50618 (Nominal) | Approx. Cable Diameter (mm) as per EN 50618 | Single cable free in air (A) | Single cable on a surface (A) | Two loaded cables touching, on a surface (A) | Max. Conductor Resistance at 20°C, (Ω/Km)
[19 empty] | 12010101xx01 | 1.5 | 0.70 | 0.80 | 4.66 | 30 | 29 | 24 | 13.7
[19 empty] | 12010102xx01 | 2.5 | 0.70 | 0.80 | 5.09 | 41 | 39 | 33 | 8.21
[19 empty] | 12010103xx01 | 4.0 | 0.70 | 0.80 | 5.59 | 55 | 52 | 44 | 5.09
[19 empty] | 12010104xx01 | 6.0 | 0.70 | 0.80 | 6.13 | 70 | 67 | 57 | 3.39
[19 empty] | 12010105xx01 | 10.0 | 0.70 | 0.80 | 7.07 | 98 | 93 | 79 | 1.95
[19 empty] | 12010106xx01 | 16.0 | 0.70 | 0.90 | 8.32 | 132 | 125 | 107 | 1.24
[19 empty] | 12010107xx01 | 25.0 | 0.90 | 1.00 | 10.14 | 176 | 167 | 142 | 0.795
[19 empty] | 12010108xx01 | 35.0 | 0.90 | 1.10 | 11.49 | 218 | 207 | 176 | 0.565
[19 empty] | 12010109xx01 | 50.0 | 1.00 | 1.20 | 13.33 | 276 | 262 | 221 | 0.393
[19 empty] | 12010110xx01 | 70.0 | 1.10 | 1.20 | 15.19 | 347 | 330 | 278 | 0.277
[19 empty] | 12010111xx01 | 95.0 | 1.10 | 1.30 | 16.94 | 416 | 395 | 333 | 0.210
[19 empty] | 12010112xx01 | 120.0 | 1.20 | 1.30 | 18.71 | 488 | 464 | 390 | 0.164
[19 empty] | 12010113xx01 | 150.0 | 1.40 | 1.40 | 20.86 | 566 | 538 | 453 | 0.132
[19 empty] | 12010114xx01 | 185.0 | 1.60 | 1.60 | 23.24 | 644 | 612 | 515 | 0.108
[19 empty] | 12010115xx01 | 240.0 | 1.70 | 1.70 | 26.14 | 755 | 736 | 620 | 0.0817
https://www.rrkabel.com/application-based-cables/power-cords-harness | POWER CORDS & HARNESS | ['https://www.rrkabel.com/Uploads/Products/130/ProductZoomForMoreDetailsImage/01.png', 'https://www.rrkabel.com/Uploads/Products/130/ProductZoomImage/two-pin-moulded.png', 'https://www.rrkabel.com/Uploads/Products/388/ProductFeaturesDetails/two-pin-moulded.png', 'https://www.rrkabel.com/Uploads/Products/388/ProductFeaturesDetails/two-pin-moulded.png'] | [15 empty] | ['The power supply cords are manufactured by using ISI marked cables. The cords are manufactured with the brass pins soldered to the cable cores. Such pins are then firstly moulded with polypropylene which offers a high degree of dielectric strength, thereafter a final layer of coloured PVC matching to the cable jacket is moulded bearing the necessary marks and approvals. The cords for the Indian market are according to the IS 1293 approval marks.'] | [9 empty] | ['We provide a wide assortment of non rewireable moulded cords. Our range offers efficient performance and durability for rugged use. These cords are tested for conformity to required standards. We can offer these cords in various sizes and specifications. These are extensively used in electronic industry, especially in TV, video games, DVD player, voltage stabiliser, heat convector, water immersions rods, instant water heaters and others electrical & electronic Home Appliances.'] | ['We also produce a wide range of two pin plugs for various applications. These cords have a wide usage on various domestic electrical and electronic appliances and gadgets on which earthing is not required. Customised moulding and cable selection is also offered. The standard offer is done with cable twin flat sheathed 0.5 Sq mm.']
[30 empty] | 120301010001 | Main Power Cords | 3 x 0.75 | 6/16 | Available in specific length as req. by Customer/Retail packs
[30 empty] | 120301020001 | Main Power Cords | 3 x 1 | 6/16 | Available in specific length as req. by Customer/Retail packs
[30 empty] | 120301030001 | Main Power Cords | 3 x 1.5 | 16 | Available in specific length as req. by Customer/Retail packs
[30 empty] | Main Power Cords | Available in specific length as req. by Customer/Retail packs
[30 empty] | 120301040001 | Main Power Cords | 2 x 0.5 | 6 | Available in specific length as req. by Customer/Retail packs
[30 empty] | Main Power Cords | Available in specific length as req. by Customer/Retail packs
[30 empty] | Main Power Cords | Available in specific length as req. by Customer/Retail packs
[30 empty] | Main Power Cords | Available in specific length as req. by Customer/Retail packs
https://www.rrkabel.com/application-based-cables/uninyvin-cable | UNINYVIN CABLE | ['https://www.rrkabel.com/Uploads/Products/131/ProductZoomForMoreDetailsImage/02.jpg', 'https://www.rrkabel.com/Uploads/Products/131/ProductZoomImage/03.jpg', 'https://www.rrkabel.com/Uploads/Products/391/ProductFeaturesDetails/01.png', 'https://www.rrkabel.com/Uploads/Products/391/ProductFeaturesDetails/01.png'] | ['These cables are used in UPS systems and server rooms as the nylon and fiber glass braid on the cable does not allows the heat generated inthe conductor, due to continuous operation, to be felt in the surrounding areas. These cables are widely used in aircraft cabling.'] | [10 empty] | ['Annealed tinned copper to IS:10241 Part 3, uniformly bunched to form a circular shape'] | ['Special core insulation HR-PVC 105° C'] | [19 empty] | ['Braided with glass fiber, 100% coverage'] | ['Braided with nylon fiber, 100% coverage'] | ['600V r.m.s.'] | ['* Denotes two cables only ** Denotes five cables only', 'Note : 1) The current rating mentioned in Table I are for bunched cables in free air at 40 °C. 2) Derating factors mentioned in Table II, shall to be used for higher ambient temperature.']
[39 empty] | 120401050001 | 14 | 2.05 | 70/0.193 | 1.956 | 1.803 | 0.279 | 0.178 | 0.076 | 3.4 | 3 | 9.2 | 31
[39 empty] | 120401060001 | 12 | 3.22 | 110/0.191 | 2.438 | 2.286 | 0.279 | 0.178 | 0.076 | 3.8 | 3.5 | 5.85 | 43
[39 empty] | 120401070001 | 10 | 5.33 | 73/0.305 | 3.15 | 2.896 | 0.381 | 0.381 | 0.127 | 5 4. | 6 | 3.532 | 61
[39 empty] | 120401080001 | 8 | 8.76 | 120/0.305 | 3.242 | 3.937 | 0.381 | 0.381 | 0.127 | 6.3 | 5.9 | 2.154 | 87
[39 empty] | 120401090001 | 6 | 13.3 | 182/0.305 | 5.537 | 5.08 | 0.381 | 0.381 | 0.127 | 7.6 | 7.3 | 1.422 | 115
[39 empty] | 120401100001 | 4 | 21.5 | 294/0.305 | 6.909 | 6.452 | 0.483 | 0.381 | 0.127 | 9.3 | 8.8 | 0.877 | 160
[39 empty] | 120401110001 | 2 | 33.3 | 203/0.457 | 8.763 | 8.128 | 0.483 | 0.381 | 0.127 | 11.0 | 10.5 | 0.565 | 200
[39 empty] | 120401120001 | 1 | 40.7 | 248/0.457 | 9.754 | 9.119 | 0.559 | 0.381 | 0.127 | 12.2 | 11.7 | 0.463 | 220
[39 empty] | 120401130001 | 0 | 53 | 323/0.457 | 10.973 | 10.338 | 0.635 | 0.381 | 0.127 | 13.7 | 13 | 0.355 | 240
[39 empty] | 120401140001 | 0 | 68.3 | 416/0.457 | 12.446 | 11.684 | 0.686 | 0.381 | 0.127 | 15.4 | 14.6 | 0.276 | 270
[40 empty] | 14 | [11 empty] | 2.05 | 31 | 24 | 17 | 12
[40 empty] | 12 | [11 empty] | 3.22 | 43 | 30 | 22 | 15
[40 empty] | 10 | [11 empty] | 5.33 | 61 | 47 | 36 | 25
[40 empty] | 8 | [11 empty] | 8.76 | 87 | 65 | 49 | 36
[40 empty] | 6 | [11 empty] | 13.3 | 115 | 87 | 65 | –
[40 empty] | 4 | [11 empty] | 21.5 | 160 | 120 | 92 | –
[40 empty] | 2 | [11 empty] | 33.3 | 200 | 155 | 120 | –
[40 empty] | 1 | [11 empty] | 40.7 | 220 | 165 | 130 | –
[40 empty] | 0 | [11 empty] | 53 | 240 | 185 | 168* | –
[40 empty] | 0 | [11 empty] | 68.3 | 270 | 210/240* | 190** | –
[40 empty] | 14 | [11 empty] | 2.05 | 50 | 47 | 43 | 42
[40 empty] | 12 | [11 empty] | 3.22 | 72 | 67 | 62 | 60
[40 empty] | 10 | [11 empty] | 5.33 | 110 | 107 | 104 | 101
[40 empty] | 8 | [11 empty] | 8.76 | 173 | 165 | 159 | 153
[40 empty] | 6 | [11 empty] | 13.3 | 250 | 236 | 230 | –
[40 empty] | 4 | [11 empty] | 21.5 | 390 | 378 | 360 | –
[40 empty] | 2 | [11 empty] | 33.3 | 545 | 530 | 520 | –
[40 empty] | 1 | [11 empty] | 40.7 | 620 | 600 | 590 | –
[40 empty] | 0 | [11 empty] | 53 | 705 | 690 | 680 | –
[40 empty] | 0 | [11 empty] | 68.3 | 820 | 810 | 800 | –
https://www.rrkabel.com/application-based-cables/application-based-cables-weldex-is-98572 | WELDEX-IS 9857 | ['https://www.rrkabel.com/Uploads/Products/132/ProductZoomForMoreDetailsImage/02.jpg', 'https://www.rrkabel.com/Uploads/Products/132/ProductZoomImage/03.jpg', 'https://www.rrkabel.com/Uploads/Products/394/ProductFeaturesDetails/01.png', 'https://www.rrkabel.com/Uploads/Products/394/ProductFeaturesDetails/01.png'] | ['For use between welding generators and hand electrodes and the workpiece .For use in automobile industries, ship building, in transport and conveyor system, tool making machinery, welding robots, etc.'] | ['Adapted to IS:9857, IS:6380, IS:8130.'] | [13 empty] | ['Super fine strands of annealed bare copper according to IS:8130, Cl. 6. Elastomeric insulation type SE-1 conforming to the requirements of IS:6380.'] | [38 empty] | ['450V a. c. rms.'] | ['1000V'] | ['-20°C to +60°C'] | ['The heavy duty welding cable is resistant to flame, oil, abrasions, tar and grease. Suitable for use in open air, in dry as well as damp interiors.The high degree of flexibility does not form knots on the cable which could lead to internal break of conductors.']
[30 empty] | 120500100016 | [30 empty] | 16 | 0.21 | 1.21 | 2 | 9.2
[30 empty] | 120500100025 | [30 empty] | 25 | 0.21 | 0.78 | 2 | 10.5
[30 empty] | 120500100035 | [30 empty] | 35 | 0.21 | 0.554 | 2 | 11.5
[30 empty] | 120500100050 | [30 empty] | 50 | 0.31 | 0.386 | 2.2 | 13.5
[30 empty] | 120500100070 | [30 empty] | 70 | 0.31 | 0.272 | 2.4 | 15.5
[30 empty] | 120500100095 | [30 empty] | 95 | 0.31 | 0.206 | 2.6 | 17.7
[39 empty] | 120500100016 | [26 empty] | 16 | 94 | 102 | 121 | 172 | 210
[39 empty] | 120500100025 | [26 empty] | 25 | 125 | 136 | 161 | 228 | 279
[39 empty] | 120500100035 | [26 empty] | 35 | 156 | 169 | 201 | 285 | 349
[39 empty] | 120500100050 | [26 empty] | 50 | 197 | 214 | 254 | 360 | 440
[39 empty] | 120500100070 | [26 empty] | 70 | 248 | 269 | 320 | 453 | 555
[39 empty] | 120500100095 | [26 empty] | 95 | 299 | 342 | 386 | 546 | 669
https://www.rrkabel.com/application-based-cables/weldex-si-single-insulated | WELDEX-SI (Single Insulated) | ['https://www.rrkabel.com/Uploads/Products/133/ProductZoomForMoreDetailsImage/02.jpg', 'https://www.rrkabel.com/Uploads/Products/133/ProductZoomImage/03.jpg', 'https://www.rrkabel.com/Uploads/Products/397/ProductFeaturesDetails/01.png', 'https://www.rrkabel.com/Uploads/Products/397/ProductFeaturesDetails/01.png'] | ['The welding cable is specially designed for the transmission of high currents from the electric welding machine to the welding tool. It is suitable for flexible use under rugged conditions, on assembly lines and conveyor systems, in machine tool and motor car manufacturing, shipbuilding and for spot welding machines.'] | [14 empty] | ['Super fine strands of annealed bare copper as per EN 60228, Cl. 6. Elastomeric PVC insulation. *Also available with TPE insulation 105°C'] | [39 empty] | ['3000V'] | ['-30°C to + 70°C'] | ['The heavy duty welding cable is resistant to flame, oil, abrasions, tar and grease. Suitable for use in open air, in dry as well as damp interiors. The high degree of flexibility does not form knots on the cable which could lead to internal break of conductors.'] | [11 empty] | ['450V a.c.r.m.s.']
[30 empty] | 1206y0100010 | [30 empty] | 10 | 0.31 | 1.91 | [9 empty] | 2 | 10 | 140
[30 empty] | 1206y0100016 | [30 empty] | 16 | 0.31 | 1.21 | [9 empty] | 2 | 11.5 | 200
[30 empty] | 1206y0100025 | [30 empty] | 25 | 0.31 | 0.78 | [9 empty] | 2 | 13 | 285
[30 empty] | 1206y0100035 | [30 empty] | 35 | 0.31 | 0.554 | [9 empty] | 2 | 14.5 | 375
[30 empty] | 1206y0100050 | [30 empty] | 50 | 0.31 | 0.386 | [9 empty] | 2.2 | 17 | 540
[30 empty] | 1206y0100070 | [30 empty] | 70 | 0.31 | 0.272 | [9 empty] | 2.4 | 19 | 740
[30 empty] | 1206y0100095 | [30 empty] | 95 | 0.31 | 0.206 | [9 empty] | 2.6 | 21.5 | 1000
[30 empty] | 1206y0100120 | [30 empty] | 120 | 0.31 | 0.161 | [9 empty] | 2.8 | 24 | 1230
[30 empty] | 1206y0100150 | [30 empty] | 150 | 0.31 | 0.129 | [9 empty] | 3 | 26 | 1500
https://www.rrkabel.com/application-based-cables/weldex-di-double-insulated | WELDEX-DI (Double Insulated) | ['https://www.rrkabel.com/Uploads/Products/134/ProductZoomForMoreDetailsImage/02.jpg', 'https://www.rrkabel.com/Uploads/Products/134/ProductZoomImage/03.jpg', 'https://www.rrkabel.com/Uploads/Products/400/ProductFeaturesDetails/01.png', 'https://www.rrkabel.com/Uploads/Products/400/ProductFeaturesDetails/01.png'] | ['Double insulated cable, for welding machines provides higher current carrying capacity. Used to conduct secondary voltage in secondary side connection to MMA welding power sources.'] | [14 empty] | ['Super fine strands of annealed bare copper as per EN 60228, Cl. 6 Elastomeric PVC composite covering. * Also available with TPE composite covering 105°C'] | [39 empty] | ['3000V'] | ['-30°C to +70°C'] | ['The heavy duty welding cable is resistant to flame, oil, abrasions, tar and grease. Suitable for use in open air, in dry as well as damp interiors. The high degree of flexibility does not form knots on the cable which could lead to internal break of conductors.'] | [11 empty] | ['450V a.c.r.m.s.']
[30 empty] | 1207y0100010 | [30 empty] | 10 | 0.3 | 1.91 | [9 empty] | 3.2 | 10 | 180
[30 empty] | 1207y0100016 | [30 empty] | 16 | 0.3 | 1.21 | [9 empty] | 3.2 | 11.5 | 250
[30 empty] | 1207y0100025 | [30 empty] | 25 | 0.3 | 0.78 | [9 empty] | 3.2 | 13 | 350
[30 empty] | 1207y0100035 | [30 empty] | 35 | 0.3 | 0.554 | [9 empty] | 3.2 | 14.5 | 460
[30 empty] | 1207y0100050 | [30 empty] | 50 | 0.3 | 0.386 | [9 empty] | 3.5 | 17 | 650
[30 empty] | 1207y0100070 | [30 empty] | 70 | 0.3 | 0.272 | [9 empty] | 3.8 | 19 | 880
[30 empty] | 1207y0100095 | [30 empty] | 95 | 0.3 | 0.206 | [9 empty] | 4.2 | 21.5 | 1170
[30 empty] | 1207y0100120 | [30 empty] | 120 | 0.3 | 0.161 | [9 empty] | 4.5 | 24 | 1430
[30 empty] | 1207y0100150 | [30 empty] | 150 | 0.3 | 0.129 | [9 empty] | 4.8 | 26 | 1720
https://www.rrkabel.com/application-based-cables/elevator-cable | ELEVATOR CABLE | ['https://www.rrkabel.com/Uploads/Products/135/ProductZoomForMoreDetailsImage/02.png', 'https://www.rrkabel.com/Uploads/Products/135/ProductZoomImage/03.jpg', 'https://www.rrkabel.com/Uploads/Products/403/ProductFeaturesDetails/01.png', 'https://www.rrkabel.com/Uploads/Products/403/ProductFeaturesDetails/01.png'] | ['These power and control flat cables can be used on festooned systems on handling equipment as overhead cranes. They are designed for indoors and outdoors for ambient temperature down to -25°C.These cables can accept a trolley traveling speed up to 120m / min.'] | ['HD 359 S2, IEC 227 Part 6, EN 50214'] | [13 empty] | ['Flexible bare copper, Class 5, IEC 60228 PVC (polyvinyl chloride) insulation PVC (polyvinyl chloride) outer sheath Cable Colour : Black *A stripping thread can be used in each group of cores. Bending Radius : Fixed installation: 8 x cable height'] | [53 empty] | ['H05VVH6-F – 300/500V', 'H07VVH6-F – 450/750V'] |  |  |  | ['Note : ***H05VVH6-F Cables']
[30 empty] | 120810401105 | [30 empty] | 4 x 1.5 | [13 empty] | 150 |  | 15.0 x 5.0
[30 empty] | 120810411105 | [30 empty] | 4 G 1.5 | [13 empty] | 150 |  | 15.0 x 5.0
[30 empty] | 120810411205 | [30 empty] | 4 G 2.5 | [13 empty] | 210 |  | 18.5 x 5.7
[30 empty] | 120810410004 | [30 empty] | 4 G 4 | [13 empty] | 300 |  | 21.0 x 6.5
[30 empty] | 120810410006 | [30 empty] | 4 G 6 | [13 empty] | 385 |  | 23.0 x 7.0
[30 empty] | 120810410010 | [30 empty] | 4 G 10 | [13 empty] | 620 |  | 28.8 x 9.0
[30 empty] | 120810410016 | [30 empty] | 4 G 16 | [13 empty] | 990 |  | 36.8 x 10.8
[30 empty] | 120810410025 | [30 empty] | 4 G 25 | [13 empty] | 1550 |  | 45.5 x 13.5
[30 empty] | 120810410035 | [30 empty] | 4 G 35 | [13 empty] | 2030 |  | 50.5 x 14.8
[30 empty] | 120810410050 | [30 empty] | 4 G 50 | [13 empty] | 2650 |  | 56.0 x 16.5
[30 empty] | 120810410070 | [30 empty] | 4 G 70 | [13 empty] | 3650 |  | 63.0 x 18.0
[30 empty] | 120810410095 | [30 empty] | 4 G 95 | [13 empty] | 4550 |  | 72.5 x 20.5
[30 empty] | 120810511105 | [30 empty] | 5 G 1.5 | [13 empty] | 180 |  | 18.0 x 5.0
[30 empty] | 120810511205 | [30 empty] | 5 G 2.5 | [13 empty] | 260 |  | 22.0 x 5.7
[30 empty] | 120810510004 | [30 empty] | 5 G 4 | [13 empty] | 380 |  | 27.0 x 6.5
[30 empty] | 120810510006 | [30 empty] | 5 G 6 | [13 empty] | 480 |  | 27.0 x 7.0
[30 empty] | 120810510010 | [30 empty] | 5 G 10 | [13 empty] | 780 |  | 34.5 x 9
[30 empty] | 120810711105 | [30 empty] | 7 G 1.5 | [13 empty] | 260 |  | 26.0 x 5.0
[30 empty] | 120810711205 | [30 empty] | 7 G 2.5 | [13 empty] | 380 |  | 32.3 x 5.7
[30 empty] | 120810710004 | [30 empty] | 7 G 4 | [13 empty] | 550 |  | 40.0 x 6.8
[30 empty] | 120810801105 | [30 empty] | 8 x 1.5 | [13 empty] | 300 |  | 29.0 x 5.0
[30 empty] | 120810811105 | [30 empty] | 8 G 1.5 | [13 empty] | 300 |  | 29.0 x 5.0
[30 empty] | 120810811205 | [30 empty] | 8 G 2.5 | [13 empty] | 405 |  | 34.5 x 5.7
[30 empty] | 120811011105 | [30 empty] | 10 G 1.5 | [13 empty] | 360 |  | 35.0 x 5.0
[30 empty] | 120811210001 | [30 empty] | 12 G 1*** | [13 empty] | 320 |  | 33.5 x 4.5
[30 empty] | 120811201105 | [30 empty] | 12 x 1.5 | [13 empty] | 420 |  | 40.5 x 5
[30 empty] | 120811211105 | [30 empty] | 12 G 1.5 | [13 empty] | 420 |  | 40.5 x 5
[30 empty] | 120811211205 | [30 empty] | 12 G 2.5 | [13 empty] | 620 |  | 50.5 x 5.7
[30 empty] | 120811210004 | [30 empty] | 12 G 4 | [13 empty] | 880 |  | 57 x 6.8
[30 empty] | 120811411105 | [30 empty] | 14 G 1.5 | [13 empty] | 490 |  | 47.5 x 5
[30 empty] | 120811611105 | [30 empty] | 16 G 1.5 | [13 empty] | 560 |  | 53.5 x 5
[30 empty] | 120811810001 | [30 empty] | 18 G 1*** | [13 empty] | 470 |  | 50.5 x 4.5
[30 empty] | 120811811105 | [30 empty] | 18 G 1.5 | [13 empty] | 620 |  | 58.0 x 5.0
[30 empty] | 120812410001 | [30 empty] | 24 G 1*** | [13 empty] | 610 |  | 6.5 x 4.5
[30 empty] | 120810401105 | [30 empty] | 4 x 1.5 | [16 empty] | 20 | 20.2
[30 empty] | 120810411105 | [30 empty] | 4 G 1.5 | [16 empty] | 20 | 20.2
[30 empty] | 120810411205 | [30 empty] | 4 G 2.5 | [16 empty] | 27 | 12.3
[30 empty] | 120810410004 | [30 empty] | 4 G 4 | [16 empty] | 36 | 7.8
[30 empty] | 120810410006 | [30 empty] | 4 G 6 | [16 empty] | 48 | 5.3
[30 empty] | 120810410010 | [30 empty] | 4 G 10 | [16 empty] | 63 | 3.2
[30 empty] | 120810410016 | [30 empty] | 4 G 16 | [16 empty] | 85 | 2
[30 empty] | 120810410025 | [30 empty] | 4 G 25 | [16 empty] | 112 | 1.3
[30 empty] | 120810410035 | [30 empty] | 4 G 35 | [16 empty] | 138 | 0.97
[30 empty] | 120810410050 | [30 empty] | 4 G 50 | [16 empty] | 168 | 0.74
[30 empty] | 120810410070 | [30 empty] | 4 G 70 | [16 empty] | 213 | 0.55
[30 empty] | 120810410095 | [30 empty] | 4 G 95 | [16 empty] | 258 | 0.42
[30 empty] | 120810511105 | [30 empty] | 5 G 1.5 | [16 empty] | 18 | 20.2
[30 empty] | 120810511205 | [30 empty] | 5 G 2.5 | [16 empty] | 25 | 12.3
[30 empty] | 120810510004 | [30 empty] | 5 G 4 | [16 empty] | 36 | 7.8
[30 empty] | 120810510006 | [30 empty] | 5 G 6 | [16 empty] | 48 | 5.3
[30 empty] | 120810510010 | [30 empty] | 5 G 10 | [16 empty] | 63 | 3.2
[30 empty] | 120810711105 | [30 empty] | 7 G 1.5 | [16 empty] | 15 | 20.2
[30 empty] | 120810711205 | [30 empty] | 7 G 2.5 | [16 empty] | 20 | 12.3
[30 empty] | 120810710004 | [30 empty] | 7 G 4 | [16 empty] | 25 | 7.8
[30 empty] | 120810801105 | [30 empty] | 8 x 1.5 | [16 empty] | 14 | 20.2
[30 empty] | 120810811105 | [30 empty] | 8 G 1.5 | [16 empty] | 14 | 20.2
[30 empty] | 120810811205 | [30 empty] | 8 G 2.5 | [16 empty] | 20 | 12.3
[30 empty] | 120811011105 | [30 empty] | 10 G 1.5 | [16 empty] | 12 | 20.2
[30 empty] | 120811210001 | [30 empty] | 12 G 1*** | [16 empty] | 8 | 38.2
[30 empty] | 120811201105 | [30 empty] | 12 x 1.5 | [16 empty] | 11 | 20.2
[30 empty] | 120811211105 | [30 empty] | 12 G 1.5 | [16 empty] | 11 | 20.2
[30 empty] | 120811211205 | [30 empty] | 12 G 2.5 | [16 empty] | 16 | 12.3
[30 empty] | 120811210004 | [30 empty] | 12 G 4 | [16 empty] | 20 | 7.8
[30 empty] | 120811411105 | [30 empty] | 14 G 1.5 | [16 empty] | 11 | 20.2
[30 empty] | 120811611105 | [30 empty] | 16 G 1.5 | [16 empty] | 10 | 20.2
[30 empty] | 120811810001 | [30 empty] | 18 G 1*** | [16 empty] | 6 | 38.2
[30 empty] | 120811811105 | [30 empty] | 18 G 1.5 | [16 empty] | 8 | 20.2
[30 empty] | 120812410001 | [30 empty] | 24 G 1*** | [16 empty] | 6 | 38.2
https://www.rrkabel.com/application-based-cables/application-based-cables-tubular-braids | TUBULAR BRAIDS | ['https://www.rrkabel.com/Uploads/Products/136/ProductZoomForMoreDetailsImage/Superex.jpg', 'https://www.rrkabel.com/Uploads/Products/136/ProductZoomImage/01.jpg', 'https://www.rrkabel.com/Uploads/Products/406/ProductFeaturesDetails/02.png', 'https://www.rrkabel.com/Uploads/Products/406/ProductFeaturesDetails/02.png'] | ['Tubular braids are used for covering and shielding. They protect the cables and electrical conductors against interference and to realize a safe data transfer.'] | [76 empty] | ['Annealed electrolytic grade copper wire.', 'Wire Diameter – 0.16 to 0.3 mm.']
[30 empty] | 12100101000c | [30 empty] | 7.9 | [19 empty] | 36 X 7 | 0.2 | 8.5 | 25
[30 empty] | 12100102000c | [30 empty] | 10.2 | [19 empty] | 36 X 9 | 0.2 | 10 | 27
[30 empty] | 12100103000c | [30 empty] | 12.45 | [19 empty] | 36 X 11 | 0.2 | 12 | 29
[30 empty] | 12100104000c | [30 empty] | 35.8 | [19 empty] | 36 X 14 | 0.3 | 25 | 70
[30 empty] | 12100105000c | [30 empty] | 51.1 | [19 empty] | 48 X 15 | 0.3 | 25 | 90
https://www.rrkabel.com/application-based-cables/bare-copper-conductor | BARE COPPER CONDUCTOR | ['https://www.rrkabel.com/Uploads/Products/137/ProductZoomForMoreDetailsImage/02.jpg', 'https://www.rrkabel.com/Uploads/Products/137/ProductZoomImage/03.jpg', 'https://www.rrkabel.com/Uploads/Products/409/ProductFeaturesDetails/01.png', 'https://www.rrkabel.com/Uploads/Products/409/ProductFeaturesDetails/01.png'] | ['The bare copper conductor are used as ground conductor, uninsulated hook up wires and jumpers.'] | ['IEC 60228, BS EN 60228.'] | [13 empty] | ['The conductor consist of annealed bare copper wire which are stranded together. The construction of the conductor is in accordance to IEC 60228 and BS EN 60228.'] | [66 empty] | ['Soft drawn plain annealed copper']
[39 empty] | 121101010000 | [46 empty] | 16 | 7 | 1.15 | 5.01 | 141
[39 empty] | 121101020000 | [46 empty] | 25 | 7 | 0.727 | 6.32 | 223
[39 empty] | 121101030000 | [46 empty] | 35 | 7 | 0.524 | 7.41 | 309
[39 empty] | 121101040000 | [46 empty] | 50 | 19 | 0.387 | 8.72 | 418
[39 empty] | 121101050000 | [46 empty] | 70 | 19 | 0.268 | 10.53 | 604
[39 empty] | 121101060000 | [46 empty] | 95 | 19 | 0.193 | 12.34 | 839
[39 empty] | 121101070000 | [46 empty] | 120 | 37 | 0.153 | 13.91 | 1059
[39 empty] | 121101080000 | [46 empty] | 150 | 37 | 0.124 | 15.45 | 1306
[39 empty] | 121101090000 | [46 empty] | 185 | 37 | 0.0991 | 17.28 | 1634
[39 empty] | 121101100000 | [46 empty] | 240 | 61 | 0.0754 | 19.84 | 2148
[39 empty] | 121101110000 | [46 empty] | 300 | 61 | 0.0601 | 22.22 | 2695
[39 empty] | 121101120000 | [46 empty] | 400 | 91 | 0.047 | 25.15 | 3446
[39 empty] | 121101130000 | [46 empty] | 500 | 91 | 0.0366 | 28.49 | 4425
[39 empty] | 121101140000 | [46 empty] | 630 | 91 | 0.0283 | 32.41 | 5723
https://www.rrkabel.com/application-based-cables/braided-strap-abcatc | BRAIDED STRAP-ABC/ATC | ['https://www.rrkabel.com/Uploads/Products/1/ProductZoomForMoreDetailsImage/Superex.jpg', 'https://www.rrkabel.com/Uploads/Products/138/ProductZoomImage/01.jpg', 'https://www.rrkabel.com/Uploads/Products/412/ProductFeaturesDetails/01.png', 'https://www.rrkabel.com/Uploads/Products/412/ProductFeaturesDetails/01.png'] | ['These are flexible braided copper & tin copper used as ground braiding tapes for batteries.'] | [14 empty] | ['Flexible braided copper/tin copper tapes consist of wires with a stringer wire diameter of 0.12 to 0.3 mm. Surface : Plain copper or Tinned.'] | [57 empty] | ['Kindly complete the part numbers by adding the suffix (in place of ‘c’) for the conductor type required: 0 = Plain/Bare Copper, 1 = Tinned Copper.'] |  |  |  | ['Annealed electrolytic grade copper wire.', 'Wire Diameter - 0.16 to 0.2 mm.'] | [10 empty] | ['Adapted to DIN 72333 Part 3.'] | ['Flexible braided copper/tin copper tapes consist of wires with a stringer wire diameter of 0.16 to 0.2 mm.'] | ['Material : Annealed electrolytic grade copper wire. Wire Diameter – 0.16 to 0.2 mm. Packing : In rings or spools or wooden drums.']
[30 empty] | 12090101000c | [50 empty] | 36 X 48 | 0.16 | 25 | 3 | [9 empty] | 35
[30 empty] | 12090102000c | [50 empty] | 36 X 69 | 0.16 | 33 | 3.2 | [9 empty] | 50
[30 empty] | 12090103000c | [50 empty] | 48 X 72 | 0.16 | 35 | 4.5 | [9 empty] | 70
[30 empty] | 12090104000c | [50 empty] | 36 X 13 | 0.2 | 18 | 1.5 | [9 empty] | 14
[30 empty] | 12090105000c | [50 empty] | 36 X 15 | 0.2 | 20 | 1.6 | [9 empty] | 16
[30 empty] | 12090106000c | [50 empty] | 36 X 19 | 0.2 | 22 | 2 | [9 empty] | 21
[30 empty] | 12090107000c | [50 empty] | 36 X 22 | 0.2 | 22 | 2.5 | [9 empty] | 25
[30 empty] | 12090108000c | [50 empty] | 36 X 31 | 0.2 | 25 | 3 | [9 empty] | 35
[30 empty] | 12090109000c | [50 empty] | 48 X 33 | 0.2 | 33 | 3.2 | [9 empty] | 50
[30 empty] | 12090110000c | [50 empty] | 48 X 47 | 0.2 | 35 | 4.5 | [9 empty] | 70
[30 empty] | 12070111000c | [50 empty] | 48 X 48 | 0.15 | 30 | 2.5 | [9 empty] | 40
[30 empty] | 12070112000c | [50 empty] | 48 X 64 | 0.15 | 33 | 2.5 | [9 empty] | 55
[30 empty] | 12070113000c | [50 empty] | 36 X 8 | 0.3 | 20 | 2 | [9 empty] | 20
[30 empty] | 12070114000c | [50 empty] | 36 X 12 | 0.3 | 25 | 2.4 | [9 empty] | 30
[30 empty] | 12070115000c | [50 empty] | 36 X 16 | 0.3 | 30 | 3 | [9 empty] | 40
[30 empty] | 12070116000c | [50 empty] | 36 X 20 | 0.3 | 30 | 3.5 | [9 empty] | 50