## Sheet1
Link | Title | Images | Description | Application | Approvals | Voltage Grade | Conductor | Insulation | Insulation Conformity | Colours | Marking | Cable Design Parameters | ('Part Number', 'Part Number') | ('Nominal Cross Sectional Area (Sq. mm)', 'Nominal Cross Sectional Area (Sq. mm)') | ('Nominal Insulation Thickness (mm)', 'Nominal Insulation Thickness (mm)') | ('Number *Nominal Dia. of Strands', 'Number *Nominal Dia. of Strands') | ('Approx. Overall Diameter (mm)', 'Approx. Overall Diameter (mm)') | ('Max. DC Conductor Resistance at 20°C (Ω/km)', 'Max. DC Conductor Resistance at 20°C (Ω/km)') | ('Current Rating (Amps)', 'Casing') | ('Current Rating (Amps)', 'Concealed') | Conductor : | Conductor Speciality | Cable Code | Voltage Grade: | Properties | Screened Core for Video signal | Screen | Sheath | Power Cores | Part Number | Cable Type | Cable Size (Sq. mm) | Approx. Cable Diameter (mm) | Power Core Colour | Braiding | Jacket | ('Construction Details', 'Construction Details', 'Part Number') | ('Construction Details', 'Construction Details', 'Part Number.1') | ('Cable Type – Armoured', 'RG 59 F', '010501050791') | ('Cable Type – Armoured', 'RG 6 F*', '010501060791') | ('Cable Type – Armoured', 'RG 11 F', '010501070791') | Specifications | Twisted Pairs | Part Numbers | Size (mm) | No. of Pairs | Approx. Overall Diameter (mm) | ('Electrical Parameters', 'Electrical Parameters') | ('Size', '0.5 mm') | ('Size', '0.4 mm') | Cable Construction | Colour Code | 0 | 1 | 2 | 3 | Mechanical and Environmental Properties | Applicable International Standards for Cable Construction | ('Electrical Characteristics at 20°C', 'Electrical Characteristics at 20°C') | ('Specification', 'Specification') | ('Typical Performance', 'CAT 5e') | ('Typical Performance', 'CAT 6') | Frequency (MHz) | Frequency (MHz).1 | 1 | 4 | 10 | 16 | 20 | 31.25 | 62.5 | 100 | 155 | 200 | 300 | 350 |  | Colour Availability | Equivalent AWG | Nominal Cross Sectional Area (Sq. mm) | Max. DC Conductor Resistance at 20°C (Ω/km) | Maximum Overall Dimensions (W X H) (mm) | Wire Size | 2Ω load | 4Ω load | 6Ω load | 8Ω load | Voltage Rating: | Temperature Range | Minimum Bending Radius | No. of Pairs x Nominal Conductor Diameter (mm) | Approx. Copper Weight (kg/km) | Approx. Cable Weight (kg/km) | Standard | Voltage Rating | Harmonized Code | Nominal Insulation Thickness (mm) | Overall Diameter Lower Limit (mm) | Overall Diameter Upper Limit (mm) | Approx. Net Weight (kg/km) | Harmonised Designation | Technical Data | Insulation Colours | Nominal Sheath Thickness (mm) | Insulation Colour | Approx Overall Diameter (mm) | Core Colour | Sheath Colour | Product Type | Maximum Overall Dimension (W x H) (mm x mm) | Conductor : | Core Colour | Sheath Colour | Voltage grade | Speci?cations | ('Part number', 'Part number') | ('Conductor construction', 'Cross sectional area (Sq. mm)') | ('Conductor construction', 'No./Max. dia of strands (mm)') | ('Conductor resistance at 20 °C (Ω/km) Max.', 'Conductor resistance at 20 °C (Ω/km) Max.') | ('Nom. Insulation thickness (mm)', 'Nom. Insulation thickness (mm)') | ('Nominal sheath thickness (mm)', 'Nominal sheath thickness (mm)') | ('Approx. overall dimensions (W X H) (mm) +/- 0.5 mm', 'Approx. overall dimensions (W X H) (mm) +/- 0.5 mm') | ('Current carrying capacity (Ampere)', 'Current carrying capacity (Ampere)') | Ambient Temperature (°C) | Derating Factor | Core Colours | ('Conductor Construction', 'Nominal Cross Sectional Area (Sq. mm)') | ('Conductor Construction', 'No. of Strands/Max. Strands Dia. (mm)') | ('Max. Conductor Resistance at 20°C (Ω/km)', 'Max. Conductor Resistance at 20°C (Ω/km)') | ('Nominal Sheath Thickness (mm)', 'Nominal Sheath Thickness (mm)') | ('Approx. Overall Dimensions (W x H) (mm) +/- 0.5 mm', 'Approx. Overall Dimensions (W x H) (mm) +/- 0.5 mm') | ('Current Carrying Capacity (Amp.)', 'Current Carrying Capacity (Amp.)') | Conductor | Insulation | Core Colours | Sheath | Nominal Voltage | Max. Operating Temperature | Test Voltage | Cross sectionalarea (Sq. mm) | No of Strands / Max. strand dia. (mm) | Approx. overall dimensions(W X H) (mm) | Max. Conductor Resistance at 20°C (Ω/km) | Current carrying capacity (Ampere) | 4 | 5 | 6 | Breakdown Voltage | Insulation Resistance | No. of Cores & Nominal Cross Sectional Area (Sq. mm) | Approx.Cable Diameter (mm) | Approx.Copper Weight (kg/km) | Approx.Cable Weight (kg/km)
https://www.rrkabel.com/construction-building-range/superex-fr | SUPEREX FR (Flame Retardant) | ['https://www.rrkabel.com/Uploads/Products/1/ProductZoomForMoreDetailsImage/02.jpg', 'https://www.rrkabel.com/Uploads/Products/1/ProductZoomImage/03.jpg', 'https://www.rrkabel.com/Uploads/Products/1/ProductFeaturesDetails/SUPEREX-FR.png', 'https://www.rrkabel.com/Uploads/Products/1/ProductFeaturesDetails/SUPEREX-FR.png'] | ['India’s 1st REACH and RoHS Compliant Cable ¦ Flame Retardant Cable.', 'REACH, ROHS, CE and CPR Compliant Anti-Rodent, Anti-Termite 100% Electrolytic Copper More than 101% Conductivity'] | ['Suitable for wiring in all types of residential and commercial infrastructure, where fire and electrical safety is utmost important.'] | ['IS 694 marked, FIA/TAC'] | ['Up to and including 1100V'] | ['Thin strands of electrolytic copper are multi-drawn for uniformity of resistance, dimension and flexibility. The strands are twisted with high precision to impart circularity for the conductor.'] | ['Specially formulated flame retardant PVC insulation is used. The FR property retards the propagation of flame without compromising safety.'] | ['IS 5831, Type A/D FR 70', 'o', 'C'] | ['Red, yellow, blue, black, green, grey & white'] | ['The cables are printed with marking of ‘SUPEREX FR" from 1 Sq. mm to 4 Sq. mm & "RR KABEL FR" for all other sizes.'] | ['Please complete the part numbers for these cables by adding the suffix (in place of ‘xx’) for the colour required: 01 – green, 02 – black, 03 – red, 04 – blue, 05 – yellow, 06 – grey, 07 – white.', '*Conductor as per IS 8130', '** Insulation Type D as per IS 5831']
[13 empty] | 01010102xx20 | 0.75** | 0.6 | 24/0.2 | 2.3 | 26 | 9 | 8
[13 empty] | 01010103xx20 | 1 | 0.7 | 14/0.3 | 2.7 | 18.1 | 14 | 13
[13 empty] | 01010104xx20 | 1.5 | 0.7 | 22/0.3 | 3 | 12.1 | 18 | 16
[13 empty] | 01010105xx20 | 2.5 | 0.8 | 36/0.3 | 3.7 | 7.41 | 24 | 20
[13 empty] | 01010106xx20 | 4** | 0.8 | 56/0.3 | 4.1 | 4.95 | 30 | 26
[13 empty] | 01010107xx20 | 6** | 0.8 | 84/0.3 | 4.6 | 3.3 | 38 | 33
[13 empty] | 01010108xx20 | 10** | 1 | 140/0.3 | 7 | 1.91 | 52 | 45
[13 empty] | 01010109xx20 | 16** | 1 | 126/0.4 | 8.1 | 1.21 | 70 | 60
https://www.rrkabel.com/construction-building-range/flamex-fr-lsh | FLAMEX FRLS (Flame Retardant Low Smoke) | ['https://www.rrkabel.com/Uploads/Products/2/ProductZoomForMoreDetailsImage/02.jpg', 'https://www.rrkabel.com/Uploads/Products/2/ProductZoomImage/03.jpg', 'https://www.rrkabel.com/Uploads/Products/4/ProductFeaturesDetails/01.png', 'https://www.rrkabel.com/Uploads/Products/4/ProductFeaturesDetails/01.png'] | ['India’s 1st REACH and RoHS Compliant Cable ¦ Flame Retardant Low Smoke Low Halogen.', 'REACH, ROHS, CE and CPR Compliant Anti-Rodent, Anti-Termite 100% Electrolytic Copper More than 101% Conductivity'] | ['Suitable for use in conduit and for fixed, protected installation particularly suitable for wiring in fire and explosion prone areas, chemical factories, densely wired areas, public buildings, schools, hospitals, commercial complexes, theatres, etc.'] | ['IS 694 marked, FIA/TAC'] | ['Up to and including 1100V'] | ['Thin strands of electrolytic copper are multi-drawn for uniformity of resistance, dimension and flexibility'] | ['Specially formulated flame retardant low smoke low halogen compound to restrict the spread of flames in fire situation. The smoke emitted by the burning cable is considerably low compared to traditional cables. This ensures improved visibility for evacuation of trapped victims and facilitates fire fighting operation.'] | ['IS 5831 Type A/D FR-LSH 70°C'] | ['Entire cable has white base and a double strip of Green, Black, Red, Yellow, Blue, Grey, running along the cable length'] | ['The cables are printed with the marking of "FLAMEX FR-LSH’'] | ['Kindly complete the part numbers for these cables by adding the suffix (in place of ‘xx’) for the colour required: 01 – green, 02 – black, 03 – red, 04 – blue, 05 – yellow, 06 – grey.', '*Conductor as per IS 8130. **Insulation Type D as per IS 5831.']
[13 empty] | 01020101xx50 | 1 | 0.7 | 14/0.3 | 2.7 | 18.1 | 14 | 13
[13 empty] | 01020102xx50 | 1.5 | 0.7 | 22/0.3 | 3 | 12.1 | 18 | 16
[13 empty] | 01020103xx50 | 2.5 | 0.8 | 36/0.3 | 3.7 | 7.41 | 24 | 20
[13 empty] | 01020104xx50 | 4** | 0.8 | 56/0.3 | 4.1 | 4.95 | 30 | 26
https://www.rrkabel.com/construction-building-range/unilay-hr-fr | UNILAY HRFR (Heat Resistant Flame Retardant) | ['https://www.rrkabel.com/Uploads/Products/3/ProductZoomForMoreDetailsImage/02.jpg', 'https://www.rrkabel.com/Uploads/Products/3/ProductZoomImage/03.jpg', 'https://www.rrkabel.com/Uploads/Products/7/ProductFeaturesDetails/01.png', 'https://www.rrkabel.com/Uploads/Products/7/ProductFeaturesDetails/01.png'] | ['India’s 1st Heat Resistant and Flame Retardant REACH and RoHS Compliant Cable with Unilay Conductor. No Loose Contacts, No Broken Ends ¦ No Sparking and Overheating.', 'REACH, ROHS, CE and CPR Compliant Anti-Rodent, Anti-Termite 100% Electrolytic Copper More than 101% Conductivity'] | ['Suitable for use in conduit and for fixed, protected installation, ideal for high density wiring.'] | ['IS 694 marked, FIA / TAC'] | ['Up to and including 1100V'] |  | ['Specially formulated heat resistant & flame retardant PVC insulation is used. The HR FR property retards the propagation of flame without compromising safety.'] | ['IS 5831, Type C - HR 85°C + FR'] | ['Green, Black, Red, Yellow, Blue, Grey, White'] | ['The cables are printed with marking of "RR-UNILAY HR FR’'] | ['Kindly complete the part numbers for these cables by adding the suffix (in place of ‘xx’) for the colour required: 01 – green, 02 – black, 03 – red, 04 – blue, 05 – yellow, 06 – grey, 07 – white.', '*Conductor as per IS 8130'] | [8 empty] | ['Thin strands of electrolytic copper are multi-drawn for uniformity of resistance, dimension and flexibility. The drawn strands are uni-laid with high precision and compacted. Thus forming a perfectly circular conductor which enables reduction in overall diameter for space saving in high density wiring.'] | ['The strands do not get cut when stripping the insulation. The conductor offers perfect contact at pins, terminals and sockets. Thus, eliminating spot heating and sparking.']
[13 empty] | 01030101xx40 | 1 | 0.7 | 37/0.20 | 2.6 | 19.5 | 14 | 13
[13 empty] | 01030102xx40 | 1.5 | 0.7 | 37/0.22 | 3 | 13.3 | 18 | 16
[13 empty] | 01030103xx40 | 2.5 | 0.8 | 61/0.22 | 3.6 | 7.98 | 24 | 20
[13 empty] | 01030104xx40 | 4 | 0.8 | 61/0.30 | 4.1 | 4.95 | 32 | 26
[13 empty] | 01030105xx40 | 6 | 0.8 | 91/0.29 | 4.6 | 3.3 | 38 | 33
https://www.rrkabel.com/construction-building-range/firex-ls0h | FIREX LS0H (Low Smoke Zero Halogen) | ['https://www.rrkabel.com/Uploads/Products/4/ProductZoomForMoreDetailsImage/Firex_cs.png', 'https://www.rrkabel.com/Uploads/Products/4/ProductZoomImage/Firex_cswithname.jpg', 'https://www.rrkabel.com/Uploads/Products/10/ProductFeaturesDetails/01.png', 'https://www.rrkabel.com/Uploads/Products/10/ProductFeaturesDetails/01.png'] | ['HFFR (Halogen Free Flame Retardant) insulation 90°C ¦ Non-Toxic & Non-Corrosive ¦ Does not propagate flame & fire.', 'REACH, ROHS, CE and CPR Compliant Anti-Rodent, Anti-Termite 100% Electrolytic Copper More than 101% Conductivity'] | ['These cables are ideal for domestic applications, conduit wiring and fixed, protected installations. Apart from residential and commercial properties, these cables are best suited for Auditoriums, Hospitals, Hotels, Schools, Stadiums and all constructions for Public usage. These cables are ideal for use in environments where high-performance, reliability and safety is a norm.'] | ['IS 17048 marked, FIA/TAC'] |  | ['Strands of electrolytic annealed plain copper are multi-drawn for uniformity of resistance, dimension and flexibility.'] | ['HFI-XL 90 Crosslinked (thermoset) halogen free flame retardant.'] |  | ['Green, Black, Red, Yellow, Blue, Grey, White'] | ['The cables are marked "FIREX LS0H"'] | ['Kindly complete the part numbers for these cables by adding the suffix (in place of "xx") for the colour required', '01 - Green, 02 - Black, 03 - Red, 04 - Blue, 05 - Yellow, 06 - Grey, 07 - White'] | [10 empty] | ['XZ'] | ['Up to and including 1100V'] | ['• Temperature range: -15°C to +90°C • Max. short circuit temperature rating: 250°C • The insulation does not burn readily. • It does not melt and drip • Smoke is negligible, transparent, non-toxic • The victims trapped in fire do not suffocate and this facilitate fire fighting operations. • The cable has extended service life against the conventionally used cables. • The cable is also ozone resistant • Self-extinguishing and flame retardant according to IS 10810 P - 61']
[13 empty] | 01010101xx60 | 1.0* | 0.7 | 14/0.3 | 2.7 | 18.1 | 19 | 17
[13 empty] | 01010102xx60 | 1.5* | 0.7 | 22/0.3 | 3 | 12.1 | 24 | 21
[13 empty] | 01010103xx60 | 2.5* | 0.8 | 36/0.3 | 3.7 | 7.41 | 37 | 29
[13 empty] | 01010104xx60 | 4.0** | 0.8 | 56/0.3 | 4.1 | 4.95 | 41 | 33
[13 empty] | 01010105xx60 | 6.0** | 0.8 | 84/0.3 | 4.6 | 3.3 | 53 | 43
https://www.rrkabel.com/construction-building-range/cctv-camera-cable | CCTV CAMERA CABLE | ['https://www.rrkabel.com/Uploads/Products/5/ProductZoomForMoreDetailsImage/CCTV_CS1.jpg', 'https://www.rrkabel.com/Uploads/Products/5/ProductZoomImage/CCTV_CS_with_name.jpg', 'https://www.rrkabel.com/Uploads/Products/13/ProductFeaturesDetails/CCTV_CAMERA_CABLE.png', 'https://www.rrkabel.com/Uploads/Products/13/ProductFeaturesDetails/CCTV_CAMERA_CABLE.png'] |  | ['These cables are specifically designed to transmit complete video frequency with minimum distortion or attenuation for security and surveillance. This cable is offered in two variants viz., 4+1 and 3+1 CCTV Camera cable.'] |  |  | ['Solid electrolytic grade annealed plain copper, 0.5 mm'] | ['The insulation provided over the conductor is with high dielectric strength and low capacitance'] | [16 empty] | ['CCTV cables are designed to optimize the quality of video signals. The dense tin coated copper screen ensures complete elimination of EMI/RFI from video signals and also provides reduced DC resistance ground path. The multi stranded construction of video core offers better flexibility and reduced bending radius.'] | [] | ['Annealed tin coated copper braid screen, approx. 85% coverage'] | ['PVC'] | ['']
[30 empty] | 10801010795 | CCTV Cable 4+1 | 4C + 1C x 0.25 | 6 | RD, YL, BK, GN
[30 empty] | 10801020795 | CCTV Cable 3+1 | 3C + 1C x 0.25 | 6 | RD, YL, BL
https://www.rrkabel.com/construction-building-range/ratna-co-x | RATNA Co-Axial | ['https://www.rrkabel.com/Uploads/Products/6/ProductZoomForMoreDetailsImage/02.jpg', 'https://www.rrkabel.com/Uploads/Products/6/ProductZoomImage/03.jpg', 'https://www.rrkabel.com/Uploads/Products/16/ProductFeaturesDetails/01.png', 'https://www.rrkabel.com/Uploads/Products/16/ProductFeaturesDetails/01.png'] |  | ['High quality co-axial for cable TV network for notch free attenuation values over wide range of frequencies. The special jacketing offers increased life even in rugged conditions.'] |  |  | ['The central conductor is made of solid electrolytic grade annealed plain copper conductor, which has distinct advantages over traditional copper conductor'] | ['The insulation provided over the conductor is of foam PE'] |  |  |  | ['*RG 6 F is also available with CCS conductor and the applicable Part number shall be 010501040791.', '*RG 6 F armoured is also available with CCS conductor and the applicable Part number shall be 010501080791.'] | [14 empty] | ['Aluminium mylar tape is provided over the insulated conductor to shield the conductor and ensures disturbance free transmission of signals'] | [7 empty] | ['The braiding is generally provided with 60% coverage of ATC (Annealed Tinned Copper) / Al alloy'] | ['Specially formulated PVC, for rugged outdoor usage.']
[37 empty] | Inner conductor | Inner conductor | Copper | Copper | Copper
[37 empty] | Nominal Diameter (mm) | Nominal Diameter (mm) | 0.8 | 1.02 | 1.63
[37 empty] | Dielectric | Dielectric | Foam PE | Foam PE | Foam PE
[37 empty] | Nominal Diameter (mm) | Nominal Diameter (mm) | 3.5 | 4.5 | 7.0
[37 empty] | Outer Conductor | First | Bonded Al Tape | Bonded Al Tape | Bonded Al Tape
[37 empty] | Outer Conductor | Second | Tinned Cu/Al Braid | Tinned Cu/Al Braid | Tinned Cu/Al Braid
[37 empty] | Nominal Coverage (%) | Nominal Coverage (%) | 60 | 60 | 60
[37 empty] | PVC Jacket | PVC Jacket | Black | Black | Black
[37 empty] | Nominal Cable Diameter (mm) | Nominal Cable Diameter (mm) | 6.2 | 7.0 | 10.0
[37 empty] | Nominal Cable Diameter (mm) |  | 10.5 | 11.4 | 14.6
https://www.rrkabel.com/construction-building-range/ratnacom | RATNACOM | ['https://www.rrkabel.com/Uploads/Products/7/ProductZoomForMoreDetailsImage/RATNACOMwithoutname.png', 'https://www.rrkabel.com/Uploads/Products/7/ProductZoomImage/Ratnacom.jpg', 'https://www.rrkabel.com/Uploads/Products/21/ProductFeaturesDetails/01.png', 'https://www.rrkabel.com/Uploads/Products/21/ProductFeaturesDetails/01.png'] |  | ['Recommended for switchboard and telephone wiring in residentials and commercial infrastructure, for transmission of analog and digitalsignals, wiring in faxes, modems, alarm enunciators, data recording/acquisition systems and various communication devices.'] |  |  | ['The central conductor is made of solid electrolytic grade of copper'] | ['Premium quality grade polyethylene used on a special extruder. This offers for low attenuation.'] |  |  | ["The cables are marked ''RATNACOM FR’"] | [24 empty] | ['Specially formulated flame retardant (FR) PVC'] | [5 empty] | ['ITD-S/WS 113C'] | ['The cores are carefully twisted with optimal lays and bunched together to deliver minimised cross talk.']
[44 empty] | 10600221040 | 0.4 | 2 | 3.9
[44 empty] | 10600321040 | 0.4 | 3 | 4.3
[44 empty] | 10600421040 | 0.4 | 4 | 4.7
[44 empty] | 10600521040 | 0.4 | 5 | 5.2
[44 empty] | 10601021040 | 0.4 | 10 | 6.5
[44 empty] | 10602021040 | 0.4 | 20 | 9.2
[44 empty] | 10600221050 | 0.5 | 2 | 4.2
[44 empty] | 10600321050 | 0.5 | 3 | 4.7
[44 empty] | 10600421050 | 0.5 | 4 | 5.1
[44 empty] | 10600521050 | 0.5 | 5 | 5.7
[44 empty] | 10601021050 | 0.5 | 10 | 7
[44 empty] | 10602021050 | 0.5 | 20 | 10
[48 empty] | DC conductor resistance | 92.20 Ω/Km at 20°C max. | 143.0 Ω/Km at 20°C max.
[48 empty] | Mutual capacitance | 50 nF/km max. | 50 nF/km max.
[48 empty] | Insulation resistance in air | 10000 M-Ω/Km | 10000 M-Ω/Km
[48 empty] | Capacitance unbalance – pair to pair | 250 pF/100m max. | 250 pF/100m max.
[48 empty] | Capacitance unbalance – pair to ground | 330 pF/100m max. | 330 pF/100m max.
[48 empty] | Resistance unbalance | 5% max. | 5% max.
https://www.rrkabel.com/construction-building-range/ratnalan-cat | RATNALAN CAT 5e/6 | ['https://www.rrkabel.com/Uploads/Products/8/ProductZoomForMoreDetailsImage/02.jpg', 'https://www.rrkabel.com/Uploads/Products/8/ProductZoomImage/03.jpg', 'https://www.rrkabel.com/Uploads/Products/24/ProductFeaturesDetails/01.png', 'https://www.rrkabel.com/Uploads/Products/24/ProductFeaturesDetails/01.png'] |  | ['LAN cables are high performance cables used increasingly for modern computer network systems. These cables form the back bone of modern data transmission in industries, residential and commercial infrastructure.'] | [46 empty] | ['Conductor : Solid bare copper Insulation : High density polyethylene Pair : 2 Insulated conductors twisted together Outer Jacket : FR PVC Packing : Available in easy pull box of 100 mtr. and 305 mtr. for CAT 5e and CAT 6 is available only in 305 mtr. pack'] | ['1 Pair : White – orange stripe and orange 2 Pair : White – green stripe and green 3 Pair : White – blue stripe and blue 4 Pair : White – brown stripe and brown']
[53 empty] | Type | Type | CAT 5e | CAT 6
[53 empty] | Part Number | Part Number | 010701014094 | 010701014194
Max. Tensile Load : 10 Kgs. per simplex cable (Installation)
Min. Bend Radius : 8 x Outer Diameter (Installation) 4 x Outer Diameter (Operation)
Temp. – Installation : 0°C to +50°C
Temp. – Operation : -10°C to +60°C
ISO/IEC 11801:2002
ISO/IEC 61156-5
EN 50173 -1:2002
EN 50288-3-1
ANSI/TIA/EIA 568B-2:2002
[59 empty] | Conductor loop resistance | Max. 190/100m | 160/100m | 140/100m
[59 empty] | Conductor resistance unbalance | Max. 2% | 0.5% | 0.5%
[59 empty] | Dielectric strength | 1.0 kV DC or 0.7 kV AC for 1 min. | 100% in process test | 100% in process test
[59 empty] | Insulation resistance | >500MΩ/Kmat100-500Vtestvoltage | >500 MΩ/Km | >500 MΩ/Km
[59 empty] | Capacitance unbalance to earth | Max. 160 pF/100m | 40 pF/100m | 40 pF/100m
[59 empty] | Velocity of propagation | <534 nsec/100m at 100MHz | 496 nsec/100m at 100 MHz (NVP for hand held testers = 0.69) | 490 nsec/100m at 100 MHz (NVP for hand held testers = 0.69)
[59 empty] | Skew | Max. 40 nsec/100m at 100MHz | Max. 25 nsec/100m at 100 MHz | Max. 30 nsec/100m at 100 MHz
[59 empty] | Mean characteristic impedance | 1000 ±50 at 100 MHZ | 1000 ±30 at 100 MHZ | 1000 ±30 at 100 MHZ
[59 empty] | Coupling attenuation up to 1 Ghz | Min. 40 dB | 50 dB | 56 dB
[63 empty] | Insertion Loss (dB/100m) | Spec value | 2 | 4.1 | 6.5 | 8.2 | 9.3 | 11.7 | 17 | 22
[63 empty] | Insertion Loss (dB/100m) | Typical value | 1.8 | 3.6 | 5.8 | 7.4 | 8.3 | 10.5 | 15.3 | 19.8 | 25.4 | 29.4 | 33.4
[63 empty] | NEXT (dB) | Spec value | 65.3 | 56.3 | 50.3 | 47.3 | 45.8 | 42.9 | 38.4 | 35.4
[63 empty] | NEXT (dB) | Typical value | 73.3 | 64.3 | 58.3 | 55.2 | 53.8 | 50.9 | 46.4 | 43.3 | 40.4 | 38.8 | 37.3
[63 empty] | PSNEXT (dB) | Spec value | 62.3 | 53.3 | 47.3 | 44.2 | 42.8 | 39.9 | 35.4 | 32.3
[63 empty] | PSNEXT (dB) | Typical value | 71.3 | 62.3 | 56.3 | 53.2 | 51.8 | 48.9 | 44.4 | 41.3 | 38.4 | 36.8 | 35.3
[63 empty] | ELFEXT (dB/100m) | Spec value | 63.8 | 51.8 | 43.8 | 39.7 | 37.8 | 33.9 | 27.9 | 23.8
[63 empty] | ELFEXT (dB/100m) | Typical value | 78.8 | 66.8 | 58.8 | 54.7 | 52.8 | 48.9 | 42.9 | 38.4 | 35 | 32.8 | 31.5
[63 empty] | PSELFEXT (db/100m) | Spec value | 60.8 | 48.8 | 40.8 | 36.7 | 34.8 | 30.9 | 24.9 | 20.8
[63 empty] | PSELFEXT (db/100m) | Typical value | 76.8 | 64.8 | 56.8 | 52.7 | 50.8 | 46.9 | 40.9 | 36.8 | 33 | 30.8 | 29.5
[63 empty] | Return Loss (dB/100m) | Spec value |  | 23.1 | 25 | 25 | 25 | 23.6 | 21.5 | 20.1
[63 empty] | Return Loss (dB/100m) | Typical value | 25 | 28 | 30 | 30 | 30 | 38.6 | 26.5 | 25.1 | 23.8 | 23 | 22.8
[63 empty] | ACR (dB/100m) | Typical value | 71.5 | 60.7 | 52.5 | 47.8 | 45.5 | 40.4 | 31.1 | 23.5 | 15 | 9.4 | 3.1
[63 empty] | PSACR (dB/100m) | Typical value | 69.5 | 58.7 | 50.5 | 45.8 | 43.5 | 38.4 | 29.1 | 21.5 | 13 | 7.4 | 2
[63 empty] | Insertion Loss (dB/100m) | Spec value | 2 | 3.8 | 6 | 7.6 | 8.5 | 10.7 | 15.4 | 19.8 | 29 | 32.8
[63 empty] | Insertion Loss (dB/100m) | Typical value | 1.9 | 3.5 | 5.5 | 7 | 7.8 | 9.9 | 14.1 | 18 | 26.1 | 29.4 |  | 32.5
[63 empty] | NEXT (dB) | Spec value | 66 | 65.3 | 59.3 | 56.2 | 54.8 | 51.9 | 47.4 | 44.3 | 39.8 | 38.3
[63 empty] | NEXT (dB) | Typical value | 86.5 | 77.5 | 10.5 | 68.4 | 67 | 64.1 | 59.6 | 56.5 | 52 | 50.5 |  | 49.3
[63 empty] | PSNEXT (dB) | Spec value | 64 | 63.3 | 57.3 | 54.2 | 52.8 | 49.9 | 45.4 | 42.3 | 37.8 | 36.3
[63 empty] | PSNEXT (dB) | Typical value | 84.5 | 75.5 | 69.5 | 66.4 | 65 | 62.1 | 57.6 | 54.5 | 50 | 48.5 |  | 47.3
[63 empty] | ELFEXT (dB/100m) | Spec value | 66 | 58 | 50 | 45.9 | 44 | 40.1 | 34.1 | 30 | 24 | 22
[63 empty] | ELFEXT (dB/100m) | Typical value | 85 | 73 | 65 | 60.9 | 59 | 55.1 | 49.1 | 45 | 39 | 37 |  | 35.5
[63 empty] | PSELFEXT (db/100m) | Spec value | 64 | 55 | 47 | 42.9 | 41 | 37.1 | 31.1 | 27 | 21 | 19
[63 empty] | PSELFEXT (db/100m) | Typical value | 82 | 70 | 62 | 57.9 | 56 | 52.1 | 46.4 | 42 | 36 | 34 |  | 32.5
[63 empty] | Return Loss (dB/100m) | Spec value |  | 23 | 25 | 25 | 25 | 23.6 | 21.5 | 20.1 | 18 | 17.3
[63 empty] | Return Loss (dB/100m) | Typical value | 27 | 30 | 30 | 30 | 30 | 28.6 | 26.5 | 25.1 | 23 | 22.3 |  | 21.8
[63 empty] | ACR (dB/100m) | Typical value | 84.6 | 73.9 | 66 | 61.4 | 59.1 | 54.2 | 45.5 | 38.5 | 25.9 | 21.1 |  | 16.9
[63 empty] | PSACR (dB/100m) | Typical value | 82.6 | 10.9 | 64 | 59 | 57.1 | 52.5 | 43.5 | 36.5 | 23.9 | 19.1 |  | 14.9
https://www.rrkabel.com/construction-building-range/speaker-cable | SPEAKER CABLE | ['https://www.rrkabel.com/Uploads/Products/9/ProductZoomForMoreDetailsImage/Speaker_Cable.jpg', 'https://www.rrkabel.com/Uploads/Products/9/ProductZoomImage/Speaker_Cable_CS_with_name.jpg', 'https://www.rrkabel.com/Uploads/Products/426/ProductFeaturesDetails/SPEAKER_CABLE.png', 'https://www.rrkabel.com/Uploads/Products/426/ProductFeaturesDetails/SPEAKER_CABLE.png'] |  | ['Speaker cables are highly recommended for use in connecting speakers, public address system for clear and distortion free voice with low dB loss.'] | [46 empty] | ['Kindly complete the part numbers for these cables by adding the suffix (in place of ‘xx’) for colour required: 00 – Transparent, 02 – black'] | [25 empty] | ['The cables are manufactured with bright annealed plain flexible electrolytic grade copper conductor, bunched compactly, insulated with specially formulated PVC compound. Each core is uniquely designed for easy identification. In order to offer uniform capacitance throughout length the distance between the two conductors is maintained uniformly.'] | ['Transparent / black with red tracer for polarity identification.']
[30 empty] | 01090101xx10 | [48 empty] | 22 | 0.5 | 39 | 4.2 x 2.1
[30 empty] | 01090102xx10 | [48 empty] | 19 | 0.75 | 26 | 4.7 x 2.4
[30 empty] | 01090103xx10 | [48 empty] | 18 | 1 | 19.5 | 5.7 x 2.9
[30 empty] | 01090104xx10 | [48 empty] | 16 | 1.5 | 13.3 | 6.0 x 3.0
[30 empty] | 01090105xx10 | [48 empty] | 14 | 2.5 | 7.98 | 7.0 x 3.6
[30 empty] | 01090106xx10 | [48 empty] | 12 | 4 | 4.95 | 8.4 x 4.1
[30 empty] | 01090107xx10 | [48 empty] | 10 | 6 | 3.3 | 9.6 x 4.7
[83 empty] | 22 AWG | 3ft (0.9m) | 6ft (1.8m) | 9ft (2.7m) | 12ft (3.6m)
[83 empty] | 19 AWG | 5ft (1.5m) | 10ft (3m) | 15ft (4.5m) | 20ft (6m)
[83 empty] | 18 AWG | 8ft (2.4m) | 16ft (4.9m)) | 24ft (7.3m) | 32ft (9.7m)
[83 empty] | 16 AWG | 12ft (3.6m) | 24ft (7.3m) | 36ft (11m) | 48ft (15m)
[83 empty] | 14 AWG | 20ft (6.1m) | 40ft (12m) | 60ft (18m) | 80ft (24m)
[83 empty] | 12 AWG | 30ft (9.1m) | 60ft (18m) | 90ft (27m) | 120ft (36m)
[83 empty] | 10 AWG | 50ft (15m) | 100ft (30m) | 150ft (46m) | 200ft (61m)
https://www.rrkabel.com/construction-building-range/bus-j-ystyh | BUS J-Y(St)Yh 2 x 2 x 0.8 | ['https://www.rrkabel.com/Uploads/Products/10/ProductZoomForMoreDetailsImage/02.jpg', 'https://www.rrkabel.com/Uploads/Products/10/ProductZoomImage/03.jpg', 'https://www.rrkabel.com/Uploads/Products/427/ProductFeaturesDetails/01.png', 'https://www.rrkabel.com/Uploads/Products/427/ProductFeaturesDetails/01.png'] |  | ['Installation and operation of Building Management System requires wide range of technologies. Control, monitoring and optimization ofthe various functions and services include heating and cooling, ventilation, lighting, indicator boards, blinds and often the management ofelectric appliances. The basic control technologies have been in existence for some time. Systems are available in various degrees ofcomplexity, ranging from the timer-controlled water heater or thermo static radiator valves (TRVs), to the so-called "intelligent houses"which manage according to prearranged efficiency criteria, everything from safety and security systems to air conditioning, and fromlighting and ventilation systems to telematic services and domestic appliances.The EIB-BUS cable is used for the transmission of bus signals for intelligent automation systems in buildings.'] | [20 empty] | ['Mutual capacitance : Max. 100 nF/km.Capacitance unbalance : Max. 200 pF/100m.Characteristic impedance : 100 Ω ± 15.Max. DC Conductor Resistance (Loop) at 20°C: 73.2 Ω/kmFlame retardant to IEC 60332-1-2.These cables can be laid over, in, or below the plaster, in pipes and pipe ducts, in dry, moist and wet areas as well as outside, provided theyare protected against direct exposure to the sun. Wiring together with power supply cables is possible without limitation.', '', ''] | [51 empty] | ['Annealed Bare copper solid wire.', 'Core insulation of PVC.'] | [10 empty] | ['Max. 250V (not for power installation)'] | ['Flexing -5°C to +50°C', 'Fixed installation -30°C to +70°C'] | ['7.5 x cable ø']
[30 empty] | 11000221080 |  |  | 7.2 ± 0.5 mm | [57 empty] | 2 x 2 x 0.8 mm | 20 | 68
https://www.rrkabel.com/construction-building-range/halogen-free | HALOGEN-FREE H07Z-R-6491B | ['https://www.rrkabel.com/Uploads/Products/13/ProductZoomForMoreDetailsImage/02.jpg', 'https://www.rrkabel.com/Uploads/Products/13/ProductZoomImage/03.jpg', 'https://www.rrkabel.com/Uploads/Products/37/ProductFeaturesDetails/01.png', 'https://www.rrkabel.com/Uploads/Products/37/ProductFeaturesDetails/01.png'] |  | ['The cables are suitable for conduit wiring , especially in installations where fire, smoke and toxic fumes create potential threat.'] |  |  | ['Plain annealed copper conductor 1.5 mm.sq to 630 mm.sq stranded Cl. 2 complying with EN 60228'] | [81 empty] | ['-15°C to 90°C', 'Minimum Bending Radius'] |  |  |  |  | ['BS EN 50525-3-41.'] | ['Uo / U - 450 / 750V'] | ['1.5 mm.sq to 630 mm.sq stranded class 2 - H07Z-R']
[30 empty] | 01130101xx60 | [49 empty] | 1.5 | [16 empty] | 0.7 | 2.7 | 3.4 | 19
[30 empty] | 01130102xx60 | [49 empty] | 2.5 | [16 empty] | 0.8 | 3.3 | 4.1 | 33
[30 empty] | 01130103xx60 | [49 empty] | 4 | [16 empty] | 0.8 | 3.8 | 4.7 | 50
[30 empty] | 01130104xx60 | [49 empty] | 6 | [16 empty] | 0.8 | 4.3 | 5.4 | 74
[30 empty] | 01130105xx60 | [49 empty] | 10 | [16 empty] | 1 | 5.6 | 7 | 126
[30 empty] | 01130106xx60 | [49 empty] | 16 | [16 empty] | 1 | 6.4 | 8 | 184
[30 empty] | 01130107xx60 | [49 empty] | 25 | [16 empty] | 1.2 | 8.1 | 10.1 | 295
[30 empty] | 01130108xx60 | [49 empty] | 35 | [16 empty] | 1.2 | 9 | 11.3 | 375
[30 empty] | 01130109xx60 | [49 empty] | 50 | [16 empty] | 1.4 | 10.6 | 13.2 | 510
[30 empty] | 01130110xx60 | [49 empty] | 70 | [16 empty] | 1.4 | 12.1 | 15.1 | 710
[30 empty] | 01130111xx60 | [49 empty] | 95 | [16 empty] | 1.6 | 14.1 | 17.6 | 950
[30 empty] | 01130112xx60 | [49 empty] | 120 | [16 empty] | 1.6 | 15.6 | 19.4 | 1240
[30 empty] | 01130113xx60 | [49 empty] | 150 | [16 empty] | 1.8 | 17.3 | 21.6 | 1530
[30 empty] | 01130114xx60 | [49 empty] | 185 | [16 empty] | 2 | 19.3 | 24.1 | 1800
[30 empty] | 01130115xx60 | [49 empty] | 240 | [16 empty] | 2.2 | 22 | 27.5 | 2500
[30 empty] | 01130116xx60 | [49 empty] | 300 | [16 empty] | 2.4 | 24.5 | 30.6 | 2990
[30 empty] | 01130117xx60 | [49 empty] | 400 | [16 empty] | 2.6 | 27.5 | 34.3 | 3860
[30 empty] | 01130118xx60 | [49 empty] | 500 | [16 empty] | 2.8 | 30.5 | 38.2 | 4900
[30 empty] | 01130119xx60 | [49 empty] | 630 | [16 empty] | 2.8 | 34 | 42.5 | 6370
https://www.rrkabel.com/construction-building-range/pvc-insulated-building-wire | PVC INSULATED BUILDING WIRE (H07V-R)-6491X | ['https://www.rrkabel.com/Uploads/Products/14/ProductZoomForMoreDetailsImage/02.jpg', 'https://www.rrkabel.com/Uploads/Products/14/ProductZoomImage/03.jpg', 'https://www.rrkabel.com/Uploads/Products/40/ProductFeaturesDetails/01.png', 'https://www.rrkabel.com/Uploads/Products/40/ProductFeaturesDetails/01.png'] |  | ['The cables are suitable for power and lighting circuits and building wiring suitable for use in semi flush exposed conduits, embedded conduits and in closed installation ducts.'] |  |  | ['Plain annealed copper conductor 1.5 mm', '2', 'to 630 mm', '2', 'stranded class 2 complying with BS EN 60228, HD 383, IEC 60228'] | [81 empty] | ['-15°C to 70 °C'] | [5 empty] | ['U', '°', '/ U - 450 / 750V'] | [5 empty] | ['1.5 mm', '2', 'to 630 mm', '2', 'stranded class 2 - H07V-R'] | ['Cable Construction']
[30 empty] | 01140101xx10 | [49 empty] | 1.5 | [16 empty] | 0.7 | 2.7 | 3.3 | 19
[30 empty] | 01140102xx10 | [49 empty] | 2.5 | [16 empty] | 0.8 | 3.3 | 4 | 33
[30 empty] | 01140103xx10 | [49 empty] | 4 | [16 empty] | 0.8 | 3.8 | 4.6 | 50
[30 empty] | 01140104xx10 | [49 empty] | 6 | [16 empty] | 0.8 | 4.3 | 5.2 | 74
[30 empty] | 01140105xx10 | [49 empty] | 10 | [16 empty] | 1 | 5.6 | 6.7 | 126
[30 empty] | 01140106xx10 | [49 empty] | 16 | [16 empty] | 1 | 6.4 | 7.8 | 184
[30 empty] | 01140107xx10 | [49 empty] | 25 | [16 empty] | 1.2 | 8.1 | 9.7 | 295
[30 empty] | 01140108xx10 | [49 empty] | 35 | [16 empty] | 1.2 | 9 | 10.9 | 375
[30 empty] | 01140109xx10 | [49 empty] | 50 | [16 empty] | 1.4 | 10.6 | 12.8 | 510
[30 empty] | 01140110xx10 | [49 empty] | 70 | [16 empty] | 1.4 | 12.1 | 14.6 | 710
[30 empty] | 01140111xx10 | [49 empty] | 95 | [16 empty] | 1.6 | 14.1 | 17.1 | 950
[30 empty] | 01140112xx10 | [49 empty] | 120 | [16 empty] | 1.6 | 15.6 | 18.8 | 1240
[30 empty] | 01140113xx10 | [49 empty] | 150 | [16 empty] | 1.8 | 17.3 | 20.9 | 1530
[30 empty] | 01140114xx10 | [49 empty] | 185 | [16 empty] | 2 | 19.3 | 23.3 | 1800
[30 empty] | 01140115xx10 | [49 empty] | 240 | [16 empty] | 2.2 | 22 | 26.6 | 2500
[30 empty] | 01140116xx10 | [49 empty] | 300 | [16 empty] | 2.4 | 24.5 | 29.6 | 2990
[30 empty] | 01140117xx10 | [49 empty] | 400 | [16 empty] | 2.6 | 27.5 | 33.2 | 3860
[30 empty] | 01140118xx10 | [49 empty] | 500 | [16 empty] | 2.8 | 30.5 | 36.9 | 4900
[30 empty] | 01140119xx10 | [49 empty] | 630 | [16 empty] | 2.8 | 34 | 41.1 | 6370
https://www.rrkabel.com/construction-building-range/building-wire-6004 | 6181Y – BS 6004 | ['https://www.rrkabel.com/Uploads/Products/15/ProductZoomForMoreDetailsImage/02.jpg', 'https://www.rrkabel.com/Uploads/Products/15/ProductZoomImage/03.jpg', 'https://www.rrkabel.com/Uploads/Products/432/ProductFeaturesDetails/01.png', 'https://www.rrkabel.com/Uploads/Products/432/ProductFeaturesDetails/01.png'] |  | ['The cables are suitable for power and lighting circuits and building wiring suitable for use in semi flush exposed conduits, embeddedconduits and in closed installation ducts. Ideal for internal wiring of appliance.StandardEN 50363-3 with BS 7655-4.2 (Only for sheath).'] |  |  | ['Plain annealed copper conductor : 1.5 & 2.5 mm2 Class -1, 4.0 to 35 mm2 stranded Class 2 complying with BS EN 60228, HD 383, IEC 60228.'] | ['PVC (Polyvinyl Chloride ) compound type TI 1 complying with EN 50363-3'] | [19 empty] | ['PVC (Polyvinyl Chloride ) compound type Type 6 complying with BS 7655-4.2'] | [60 empty] | ['-15°C to 70 °C'] | ['Upto 10 mm2 : 10 X Overall Diameter.', '16 & 35 mm2 : 12 X Overall Diameter.', '16 & 35 mm2 : 12 X Overall Diameter.'] |  |  |  |  | ['1.5 mmsquare to 35 mmsquare - 300 / 500V'] | [7 empty] | ['Blue and brown']
[30 empty] | 01150101xx10 | [49 empty] | 1.5 | [16 empty] | 0.7 | 4.2 | 5 | 37 |  |  |  | 0.8
[30 empty] | 01150102xx10 | [49 empty] | 2.5 | [16 empty] | 0.8 | 4.8 | 5.7 | 51 |  |  |  | 0.8
[30 empty] | 01150103xx10 | [49 empty] | 4 | [16 empty] | 0.8 | 5.5 | 6.7 | 75 |  |  |  | 0.9
[30 empty] | 01150104xx10 | [49 empty] | 6 | [16 empty] | 0.8 | 6 | 7.3 | 98 |  |  |  | 0.9
[30 empty] | 01150105xx10 | [49 empty] | 10 | [16 empty] | 1 | 7.3 | 8.8 | 152 |  |  |  | 0.9
[30 empty] | 01150106xx10 | [49 empty] | 16 | [16 empty] | 1 | 8.4 | 10.1 | 220 |  |  |  | 1
[30 empty] | 01150107xx10 | [49 empty] | 25 | [16 empty] | 1.2 | 10 | 12.1 | 336 |  |  |  | 1.1
[30 empty] | 01150108xx10 | [49 empty] | 35 | [16 empty] | 1.2 | 11.1 | 13.5 | 353 |  |  |  | 1.1
https://www.rrkabel.com/construction-building-range/building-wire-7889 | 6181XY – BS 7889 | ['https://www.rrkabel.com/Uploads/Products/16/ProductZoomForMoreDetailsImage/02.jpg', 'https://www.rrkabel.com/Uploads/Products/16/ProductZoomImage/03.jpg', 'https://www.rrkabel.com/Uploads/Products/437/ProductFeaturesDetails/01.png', 'https://www.rrkabel.com/Uploads/Products/437/ProductFeaturesDetails/01.png'] |  | ['The cables are suitable for power and lighting circuits and building wiring suitable for use in semi flush exposed conduits, embeddedconduits and in closed installation ducts. Ideal for internal wiring of appliance.StandardBS 7889.'] |  |  | ['Plain annealed copper conductor : 4 mmsquare to 630 mmsquare stranded class 2 complying with BS EN 60228, HD 383, IEC 60228'] | ['GP8 conforming to BS 7655-1.3 ( XLPE )'] | [19 empty] | ['Type 9 specified in BS 7655-4.2'] | [60 empty] | ['-15 °C to 90°C'] | ['4.0 to 50 mmsquare : 10 X Overall diameter.', '70 & 630 mmsquare : 12 X Overall diameter.'] |  |  |  |  | ['1.5 mmsquare to 630 mmsquare - 600 / 1000V'] | [9 empty] | ['Natural']
[30 empty] | 11600100004 | [49 empty] | 4 | [16 empty] | 0.7 |  |  | 107 |  |  |  | 1.4 |  | 8
[30 empty] | 11600100006 | [49 empty] | 6 | [16 empty] | 0.7 |  |  | 132 |  |  |  | 1.4 |  | 8.5
[30 empty] | 11600100010 | [49 empty] | 10 | [16 empty] | 0.7 |  |  | 181 |  |  |  | 1.4 |  | 9.5
[30 empty] | 116001000160 | [49 empty] | 16 | [16 empty] | 0.7 |  |  | 247 |  |  |  | 1.4 |  | 10.5
[30 empty] | 11600100025 | [49 empty] | 25 | [16 empty] | 0.9 |  |  | 358 |  |  |  | 1.4 |  | 12
[30 empty] | 11600100035 | [49 empty] | 35 | [16 empty] | 0.9 |  |  | 466 |  |  |  | 1.4 |  | 13
[30 empty] | 11600100050 | [49 empty] | 50 | [16 empty] | 1 |  |  | 545 |  |  |  | 1.4 |  | 14
[30 empty] | 11600100070 | [49 empty] | 70 | [16 empty] | 1.1 |  |  | 765 |  |  |  | 1.4 |  | 16
[30 empty] | 11600100095 | [49 empty] | 95 | [16 empty] | 1.1 |  |  | 1022 |  |  |  | 1.5 |  | 18
[30 empty] | 11600100120 | [49 empty] | 120 | [16 empty] | 1.2 |  |  | 1267 |  |  |  | 1.5 |  | 20
[30 empty] | 11600100150 | [49 empty] | 150 | [16 empty] | 1.4 |  |  | 1556 |  |  |  | 1.6 |  | 22
[30 empty] | 11600100185 | [49 empty] | 185 | [16 empty] | 1.6 |  |  | 1928 |  |  |  | 1.6 |  | 24
[30 empty] | 11600100240 | [49 empty] | 240 | [16 empty] | 1.7 |  |  | 2501 |  |  |  | 1.7 |  | 27
[30 empty] | 11600100300 | [49 empty] | 300 | [16 empty] | 1.8 |  |  | 3108 |  |  |  | 1.8 |  | 29
[30 empty] | 11600100400 | [49 empty] | 400 | [16 empty] | 2 |  |  | 3923 |  |  |  | 1.9 |  | 32
[30 empty] | 11600100500 | [49 empty] | 500 | [16 empty] | 2.2 |  |  | 4999 |  |  |  | 2 |  | 36
[30 empty] | 11600100630 | [49 empty] | 630 | [16 empty] | 2.4 |  |  | 6414 |  |  |  | 2.2 |  | 40
https://www.rrkabel.com/construction-building-range/pvc-twin-core-flat-cable | PVC/PVC TWIN CORE FLAT CABLE (IS 694) | ['https://www.rrkabel.com/Uploads/Products/17/ProductZoomForMoreDetailsImage/02.jpg', 'https://www.rrkabel.com/Uploads/Products/17/ProductZoomImage/03.jpg', 'https://www.rrkabel.com/Uploads/Products/438/ProductFeaturesDetails/01.png', 'https://www.rrkabel.com/Uploads/Products/438/ProductFeaturesDetails/01.png'] |  | ['PVC 70°C cables suitable for wiring in residential and commercial infrastructure.HR PVC 85°C cables are suitable for wiring in residential and commercial infrastructure for a higher ambient temperature.FR-LSH 70°C cables are suitable for wiring in public places like schools, hospitals, theatres, etc. These are also suitable for fire prone areasand chemical factories.'] | ['IS 694 marked, FIA / TAC'] |  | ['Electrolytic grade annealed copper'] | [94 empty] | ['Variants Available'] |  |  |  |  | ['Red, black'] | ['Black, grey and white']
[42 empty] | IS 694, IS 8130 Class 1 & 2, IS 5831 Type A insulation & ST-1 sheath | [66 empty] | PVC 70°C
[42 empty] | IS 694, IS 8130 Class 1 & 2, IS 5831 Type C insulation & ST-2 sheath | [66 empty] | HR 85°C
[42 empty] | IS 694, IS 8130 Class 1 & 2, IS 5831 Type A insulation & ST-1 ( FR ) sheath | [66 empty] | FR 70°C
[42 empty] | IS 694, IS 8130 Class 1 & 2, IS 5831 Type C insulation & ST-2 (FR) sheath | [66 empty] | HR 85°C + FR
[42 empty] | IS 694, IS 8130 Class 1 & 2, IS 5831 Type A insulation & ST-1 (FR-LSH) sheath | [66 empty] | FR-LSH 70°C
[30 empty] | 0117110132yz | [49 empty] | 0.5 | [16 empty] | 0.6 | [6 empty] | 0.9 | [5 empty] | 7.2 X 4.9
[30 empty] | 0117110232yz | [49 empty] | 0.75 | [16 empty] | 0.6 | [6 empty] | 0.9 | [5 empty] | 7.8 X 5.2
[30 empty] | 0117110332yzz | [49 empty] | 1 | [16 empty] | 0.6 | [6 empty] | 0.9 | [5 empty] | 8.0 X 5.4
[30 empty] | 0117110432yz | [49 empty] | 1.5 | [16 empty] | 0.6 | [6 empty] | 0.9 | [5 empty] | 8.6 X 5.6
[30 empty] | 0117110532yz | [49 empty] | 2.5 | [16 empty] | 0.7 | [6 empty] | 1 | [5 empty] | 10.5 x 6.6
[30 empty] | 0117110632yz | [49 empty] | 4 | [16 empty] | 0.8 | [6 empty] | 1 | [5 empty] | 12.0 X 7.4
[30 empty] | 0117110732yz | [49 empty] | 6 | [16 empty] | 0.8 | [6 empty] | 1.1 | [5 empty] | 13.0 X 8.0
[30 empty] | 0117110832yz | [49 empty] | 10 | [16 empty] | 1 | [6 empty] | 1.4 | [5 empty] | 16.0 X 9.6
[30 empty] | 0117110932yz | [49 empty] | 16 | [16 empty] | 1 | [6 empty] | 1.4 | [5 empty] | 18.5 X 11.0
[30 empty] | 0117111032yz | [49 empty] | 25 | [16 empty] | 1.2 | [6 empty] | 2 | [5 empty] | 22.5 X 13.0
[30 empty] | 0117111132yz | [49 empty] | 35 | [16 empty] | 1.2 | [6 empty] | 2 | [5 empty] | 25.5 X 14.5
[30 empty] | 0117111232yz | [49 empty] | 50 | [16 empty] | 1.4 | [6 empty] | 2.2 | [5 empty] | 29.0 X 16.5
https://www.rrkabel.com/construction-building-range/pvc-3core-submersible-flat-cable | PVC/PVC 3 CORE SUBMERSIBLE FLAT CABLE | ['https://www.rrkabel.com/Uploads/Products/18/ProductZoomForMoreDetailsImage/CS.png', 'https://www.rrkabel.com/Uploads/Products/18/ProductZoomImage/CSwithName.jpg', 'https://www.rrkabel.com/Uploads/Products/440/ProductFeaturesDetails/01.png', 'https://www.rrkabel.com/Uploads/Products/440/ProductFeaturesDetails/01.png'] |  | ['The PVC insulated and sheathed 3 core flat cables are mainly used in pump connections. They are also used in many industrial applications. The sheath is specially made out to resist tough and difficult outdoor conditions & excellent resistant to water.'] | ['IS 694 marked, FIA/TAC'] | [6 empty] | ['Kindly complete the part numbers for these cables by adding the suffix (in place of ‘y’) for the cable type 1 – PVC 70°C, 3 – PVC HR 85°C.', '*Conductor configuration offered for 1.5 Sq mm-22/0.3 mm, 2.5 Sq mm – 36/0.3 mm (max.), class 2 as per IS 8130'] | [98 empty] | ['Electrolytic grade annealed copper'] | ['Red, yellow (centre core), blue'] | ['Black'] | ['Upto and including 1100v']
[109 empty] | PVC 70°C | [5 empty] | IS 694, IS 8130 Class 2(1.5 & 2.5 Sq. mm), for others class 5, IS 5831 Type A insulation & ST-1 sheath.
[109 empty] | HR 85°C | [5 empty] | IS 694, IS 8130 Class 2(1.5 & 2.5 Sq. mm), for others class 5, IS 5831 Type C insulation & ST-2 sheath.
[116 empty] | 0118110102y1 | 0.5 | 16/0.2 | 39 | 0.6 | 0.9 | 9.60 X 4.90 | 4
[116 empty] | 0118110202y1 | 0.75 | 24/0.2 | 26 | 0.6 | 0.9 | 10.5 X 5.20 | 7
[116 empty] | 0118110302y1 | 1 | 32/0.2 | 19.5 | 0.6 | 0.9 | 11.0 X 5.40 | 12
[116 empty] | 0118110402y1 | 1.5* | 22/0.3 | 12.1 | 0.6 | 0.9 | 12.0 X 5.6 | 18
[116 empty] | 0118110502y1 | 2.5* | 36/0.3 | 7.41 | 0.7 | 1 | 13.0 X 6.2 | 24
[116 empty] | 0118110602y1 | 4 | 56/0.3 | 4.95 | 0.8 | 1 | 15.3 X 7.1 | 28
[116 empty] | 0118110702y1 | 6 | 84/0.3 | 3.3 | 0.8 | 1.1 | 19.2 X 8.4 | 36
[116 empty] | 0118110802y1 | 10 | 140/0.3 | 1.91 | 1 | 1.4 | 24.2 X 10.4 | 48
[116 empty] | 0118110902y1 | 16 | 126/0.4 | 1.21 | 1 | 1.4 | 29.0 X 12.4 | 64
[116 empty] | 0118111002y1 | 25 | 196/0.4 | 0.78 | 1.2 | 2 | 36.5 X 15.7 | 80
[116 empty] | 0118111102y1 | 35 | 276/0.4 | 0.554 | 1.2 | 2 | 40.5 X 17.2 | 100
[116 empty] | 0118111202y1 | 50 | 396/0.4 | 0.386 | 1.4 | 2.2 | 46.5 X 19.3 | 130
[116 empty] | 0118111302y1 | 70 | 360/0.5 | 0.272 | 1.4 | 2.2 | 52.0 X 21.0 | 192
[116 empty] | 0118111402y1 | 95 | 480/0.5 | 0.206 | 1.6 | 2.4 | 61.0 X 24.5 | 230
[124 empty] | 25 | 1.25
[124 empty] | 30 | 1.16
[124 empty] | 35 | 1.09
[124 empty] | 40 | 1
[124 empty] | 45 | 0.9
[124 empty] | 50 | 0.81
[124 empty] | 55 | 0.74
[124 empty] | 60 | 0.68
https://www.rrkabel.com/construction-building-range/xlpe-pvc-3core-submersible-flat-cable | XLPE/PVC 3 CORE SUBMERSIBLE FLAT CABLE | ['https://www.rrkabel.com/Uploads/Products/19/ProductZoomForMoreDetailsImage/CS.png', 'https://www.rrkabel.com/Uploads/Products/19/ProductZoomImage/CSwithName.jpg', 'https://www.rrkabel.com/Uploads/Products/442/ProductFeaturesDetails/01.png', 'https://www.rrkabel.com/Uploads/Products/442/ProductFeaturesDetails/01.png'] |  | ['These cables are mainly used in pump connection. Though they are mainly used to supply power to pumps, they are also used in industrial applications. These cables are specially manufactured keeping in mind the severe, tough and difficult conditions in which they are used.'] |  |  | ['Electrolytic grade annealed plain copper to EN 60228, uniformly bunched to form a circular shape'] | [16 empty] | ['Upto and inducting 1100V'] | [83 empty] | ['Black'] | [17 empty] | ['Red, yellow (centre core), blue']
[109 empty] | XLPE/PVC | [5 empty] | Class 2(1 to 2.5 Sq. mm) for others class 5 to EN 60228, XLPE insulation & PVC ST-2 sheath to IEC 60502-1
[13 empty] | 11910300001 |  | 0.7 | [111 empty] | 1 | 14/0.3 | 18.1 | 1 | 10.6 X 5.2 | 12
[13 empty] | 11910301105 |  | 0.7 | [111 empty] | 1.5 | 22/0.3 | 12.1 | 1 | 11.6 X 5.5 | 20
[13 empty] | 11910301205 |  | 0.7 | [111 empty] | 2.5 | 36/0.3 | 7.41 | 1.1 | 13.1 X 6.2 | 30
[13 empty] | 11910300004 |  | 0.8 | [111 empty] | 4 | 56/0.3 | 4.95 | 1.1 | 15.0 X 6.8 | 37
[13 empty] | 11910300006 |  | 0.8 | [111 empty] | 6 | 84/0.3 | 3.3 | 1.2 | 17.2 X 7.7 | 46
[13 empty] | 11910300010 |  | 0.8 | [111 empty] | 10 | 140/0.3 | 1.91 | 1.3 | 20.2 X 8.8 | 66
[13 empty] | 11910300016 |  | 0.8 | [111 empty] | 16 | 126/0.4 | 1.21 | 1.4 | 23.6 X 10.0 | 85
[13 empty] | 11910300025 |  | 1 | [111 empty] | 25 | 196/0.4 | 0.78 | 1.5 | 28.9 X 12.0 | 113
[13 empty] | 11910300035 |  | 1 | [111 empty] | 35 | 276/0.4 | 0.554 | 1.6 | 32.7 X 13.4 | 139
[13 empty] | 11910300050 |  | 1.2 | [111 empty] | 50 | 396/0.4 | 0.386 | 1.7 | 38.7 X 15.5 | 156
[124 empty] | 25 | 1.16
[124 empty] | 30 | 1.11
[124 empty] | 35 | 1.06
[124 empty] | 40 | 1
[124 empty] | 45 | 0.95
[124 empty] | 50 | 0.88
[124 empty] | 55 | 0.82
[124 empty] | 60 | 0.78
[124 empty] | 65 | 0.74
[124 empty] | 70 | 0.71
[124 empty] | 75 | 0.67
[124 empty] | 80 | 0.64
https://www.rrkabel.com/ProductsDetails/index/173 | XLPE/PVC 3 CORE SUBMERSIBLE FLAT CABLE With Wall | ['https://www.rrkabel.com/Uploads/Products/173/ProductZoomForMoreDetailsImage/CSwithoutname.png', 'https://www.rrkabel.com/Uploads/Products/173/ProductZoomImage/CS.jpg', 'https://www.rrkabel.com/Uploads/Products/492/ProductFeaturesDetails/SUBMERSIBLE.png', 'https://www.rrkabel.com/Uploads/Products/492/ProductFeaturesDetails/SUBMERSIBLE.png'] | ['These submersible flat cable are specially designed to provide distinguished tube like structure for the insulated cores.The wall between the cores perfectly separate them from coming in contact with each other and provides better mechanical and electricalstrength compared to the traditional submersible flat cables. The knurling on the outer surface makes the cable more durable and provides improved abrasion resistance during handling and installationof these cables.'] | ['These cables are mainly used in submersible pump connections. These cables are specially designed keeping in mind the tough and severe conditions in which they are used.'] | [128 empty] | ['Electrolytic annealed plain copper, IS 8130'] | ['Cross-linked Polyethylene (XLPE)'] | ['Red, Yellow (Center Core), Blue'] | ['PVC, Type ST 2, IS 5831'] | ['1100 V'] | ['90°C'] | ['3 kV for 5 min.']
[97 empty] | 0.7 | [6 empty] | 0.9 | [35 empty] | 1.5 | 22/0.3 | 12.4 x 5.0 | 12.1 | 20
[97 empty] | 0.7 | [6 empty] | 1 | [35 empty] | 2.5 | 36/0.3 | 14.3 x 6.1 | 7.41 | 30
[97 empty] | 0.8 | [6 empty] | 1 | [35 empty] | 4 | 56/0.3 | 16.3 x 6.9 | 4.95 | 37
[97 empty] | 0.8 | [6 empty] | 1.1 | [35 empty] | 6 | 84/0.3 | 18.0 x 7.2 | 3.3 | 46
[53 empty] | Ambient Temperature (°C) | 25 | 30 | 35 | [88 empty] | 40 | 45 | 50
[53 empty] | Factor | 1.16 | 1.11 | 1.06 | [88 empty] | 1 | 0.95 | 0.88
https://www.rrkabel.com/construction-building-range/steel-braided-ysy | STEEL BRAIDED YSY 1.1 KV | ['https://www.rrkabel.com/Uploads/Products/20/ProductZoomForMoreDetailsImage/02.jpg', 'https://www.rrkabel.com/Uploads/Products/20/ProductZoomImage/03.jpg', 'https://www.rrkabel.com/Uploads/Products/444/ProductFeaturesDetails/01.png', 'https://www.rrkabel.com/Uploads/Products/444/ProductFeaturesDetails/01.png'] |  | ['These cables are used as power cables in building and commercial infrastructure, tool machinery, plant installation. The braided screen offers best possible protection against mechanical damage. The galvanized coating on the steel wire braiding not only helps protect against corrosion, but also notably improves the soldering performance. The transparent sheath gives the cable in addition an optical revaluation.'] | [20 empty] | ['PVC self-extinguishing and flame retardant according to IEC 60332-1-2.', ''] | [25 empty] | ['Electrolytic grade bare copper, fine wire conductors to IS 8130, Class 5. Core insulation of PVC A, IS 5831. Cores stranded with optimal lay-length. Special PVC inner jacket. Galvanised steel wire braid screen. Special transparent PVC outer jacket (Also available in Grey)'] | [25 empty] | [] | [11 empty] | ['Flexing -5°C to +70°C. Fixed installation -15°C to +70°C'] |  |  |  |  | ['The cables are provided with enhanced insulation thickness meeting 1.1kV rating.'] | [42 empty] | ['1100V'] |  | ['4000V'] | [8 empty] | ['Min. 8000V'] | ['Min. 20 GΩ x cm']
[53 empty] | No. of Cores | Colour Codes
[53 empty] | 2 | RD/BK
[53 empty] | 3 | RD/BK/GNYE
[53 empty] | 3a | RD/YL/BL
[53 empty] | 4 | RD/YL/BL/GNYE
[53 empty] | 4a | RD/YL/BL/Bk
[53 empty] | 5 | RD/YL/BL/BK/GY
[30 empty] | 01200101xx1z | [119 empty] | 2 x 1 | 9.5 | 18.3 | 162.9
[30 empty] | 01200102xx1z | [119 empty] | 3 x 1 | 9.9 | 27.4 | 183.7
[30 empty] | 01200103xx1z | [119 empty] | 4 x 1 | 10.5 | 36.5 | 212.8
[30 empty] | 01200104xx1z | [119 empty] | 5 x 1 | 11.5 | 45.6 | 251.6
[30 empty] | 01200105xx1z | [119 empty] | 2 x 1.5 | 10 | 26.7 | 187.9
[30 empty] | 01200106xx1z | [119 empty] | 3 x 1.5 | 10.5 | 40.1 | 213.7
[30 empty] | 01200107xx1z | [119 empty] | 4 x 1.5 | 11.4 | 53.5 | 256.3
[30 empty] | 01200108xx1z | [119 empty] | 5 x 1.5 | 12.2 | 66.9 | 296.8
[30 empty] | 01200109xx1z | [119 empty] | 2 x 2.5 | 11.5 | 44.6 | 252.6
[30 empty] | 01200110xx1z | [119 empty] | 3 x 2.5 | 12 | 66.9 | 292.1
[30 empty] | 01200111xx1z | [119 empty] | 4 x 2.5 | 12.9 | 89.2 | 347.2
[30 empty] | 01200112xx1z | [119 empty] | 5 x 2.5 | 13.9 | 111.4 | 407.8
[30 empty] | 01200113xx1z | [119 empty] | 2 x 4 | 12.9 | 71.9 | 334
[30 empty] | 01200114xx1z | [119 empty] | 3 x 4 | 13.6 | 107.8 | 392.3
[30 empty] | 01200115xx1z | [119 empty] | 4 x 4 | 14.6 | 143.8 | 470.9
[30 empty] | 01200116xx1z | [119 empty] | 5 x 4 | 16 | 179.7 | 567.3
[30 empty] | 01200117xx1z | [119 empty] | 2 x 6 | 14.2 | 107.8 | 420.7
[30 empty] | 01200118xx1z | [119 empty] | 3 x 6 | 15.1 | 161.8 | 510.7
[30 empty] | 01200119xx1z | [119 empty] | 4 x 6 | 16.3 | 215.7 | 619.4
[30 empty] | 01200120xx1z | [119 empty] | 2 x 10 | 17.2 | 179.7 | 627.9
[30 empty] | 01200121xx1z | [119 empty] | 3 x 10 | 18.3 | 269.6 | 769.9
[30 empty] | 01200122xx1z | [119 empty] | 4 x 10 | 19.9 | 359.5 | 940.9
[30 empty] | 01200123xx1z | [119 empty] | 2 x 16 | 19.7 | 287.6 | 862.2
[30 empty] | 01200124xx1z | [119 empty] | 3 x 16 | 20.8 | 431.4 | 1059.4
[30 empty] | 01200125xx1z | [119 empty] | 4 x 16 | 22.7 | 575.2 | 1311
[30 empty] | 01200126xx1z | [119 empty] | 2 x 25 | 23 | 447.4 | 1218.8
[30 empty] | 01200127xx1z | [119 empty] | 3 x 25 | 24.6 | 671 | 1531.3
[30 empty] | 01200128xx1z | [119 empty] | 4 x 25 | 27.1 | 894.7 | 1923.2
[30 empty] | 01200129xx1z | [119 empty] | 2 x 35 | 25.7 | 629.9 | 1585
[30 empty] | 01200130xx1z | [119 empty] | 3 x 35 | 27.3 | 944.9 | 1990.7
[30 empty] | 01200131xx1z | [119 empty] | 2 x 35 | 30.1 | 1259.9 | 2513.2
[30 empty] | 01200132xx1z | [119 empty] | 2 x 50 | 30.3 | 903.8 | 2211.6
[30 empty] | 01200133xx1z | [119 empty] | 3 x 50 | 32.2 | 1355.8 | 2789.8
[30 empty] | 01200134xx1z | [119 empty] | 4 x 50 | 35.2 | 1807.7 | 3502.1
[30 empty] | 01200135xx1z | [119 empty] | 2 x 70 | 34.1 | 1283.9 | 2923.8
[30 empty] | 01200136xx1z | [119 empty] | 3 x 70 | 36.2 | 1925.8 | 3721.4
[30 empty] | 01200137xx1z | [119 empty] | 4 x 70 | 39.7 | 2567.7 | 4695.7
[30 empty] | 01200138xx1z | [119 empty] | 2 x 95 | 38.5 | 1711.8 | 3795.5
[30 empty] | 01200139xx1z | [119 empty] | 3 x 95 | 41 | 2567.7 | 4853
[30 empty] | 01200140xx1z | [119 empty] | 4 x 95 | 45.1 | 3423.6 | 6138.5
[30 empty] | 01200141xx1z | [119 empty] | 2 x 120 | 41.8 | 2168.3 | 4603.2
[30 empty] | 01200142xx1z | [119 empty] | 3 x 120 | 44.5 | 3252.5 | 5920.2
[30 empty] | 01200143xx1z | [119 empty] | 4 x 120 | 49 | 4336.6 | 7513.4
[30 empty] | 01200144xx1z | [119 empty] | 2 x 150 | 45.9 | 2674.7 | 5591.7
[30 empty] | 01200145xx1z | [119 empty] | 3 x 150 | 48.9 | 4012.1 | 7211.7
[30 empty] | 01200146xx1z | [119 empty] | 4 x 150 | 53.9 | 5349.4 | 9166.2
[30 empty] | 01200147xx1z | [119 empty] | 2 x 185 | 50.6 | 3320.2 | 6848.6
[30 empty] | 01200148xx1z | [119 empty] | 3 x 185 | 53.9 | 4980.3 | 8849.2
[30 empty] | 01200149xx1z | [119 empty] | 4 x 185 | 59.5 | 6640.4 | 11267.5
[30 empty] | 01200150xx1z | [119 empty] | 2x 240 | 56.4 | 4279.6 | 8639.7
[30 empty] | 01200151xx1z | [119 empty] | 3 x 240 | 60.2 | 6419.3 | 11207.5
[30 empty] | 01200152xx1z | [119 empty] | 3 x 240 | 66.4 | 8559.1 | 14288.1