## Sheet1
Link | Title | Images |  | Ratnaflex -M: | Ratnaflex -M HR: | Ratnaflex -M FR: | Ratnaflex -M HRFR: | Approvals | Conductor | Standard Cable Colour | Voltage Rating | Variants Available | Product Type/Legends | Specifications | 0 | 1 | 2 | Part Number | No. of Cores | Nominal Cross Sectional Area(Sq. mm) | Nominal Insulation Thickness (mm) | Max. D.C. Conductor Resistance at 20°C(?/km) | Nominal Thickness of Sheath | Maximum Overall Dimensions (mm) | Application | Technical Data | Product Type | Nominal Cross Sectional Area (Sq. mm) | Nominal Thickness of Insulation (mm) | Nominal Thickness of Sheath (mm) | Standard | Nominal Voltage | Insulation Resistance | Temperature Range | Minimum Bending Radius: | Test Voltage | Cable Construction | Properties | Cable Design Parameters | ('Unnamed: 0_level_0', 'Part Number') | ('Part Number', 'No. of Cores and Nominal Cross Sectional Area (Sq. mm)') | ('No. of Cores and Nominal Cross Sectional Area (Sq. mm)', 'Approx. Cable Diameter (mm)') | ('Approx. Cable Diameter (mm)', 'Unnamed: 3_level_1') | ('Unnamed: 4_level_0', 'Unnamed: 4_level_1') | ('Cable Type', 'Cable Type') | ('Size Range', 'BASEC') | ('Size Range', 'VDE') | ('Size Range', 'Unnamed: 3_level_1') | No. of Cores and Nominal Cross Sectional Area (Sq. mm) | Approx. Cable Diameter (mm) | Minimum Bending Radius | Unnamed: 0 | Breakdown Voltage | ('Part Number', 'Part Number') | ('No. of Cores and Nominal Cross Sectional Area (Sq. mm)', 'No. of Cores and Nominal Cross Sectional Area (Sq. mm)') | ('Approx. Cable Diameter (mm)', 'Approx. Cable Diameter (mm)') | ('Approx. Copper Weight (kg/km)', 'Approx. Copper Weight (kg/km)') | ('Approx. Cable Weight (kg/km)', 'Approx. Cable Weight (kg/km)') | ('No. of Cores and Nominal Cross Sectional Area (Sq. mm)', 'No. of Cores and Nominal Cross Sectional Area (Sq. mm)') | ('Approx. CopperWeight (kg/km)', 'Approx. CopperWeight (kg/km)') | ('Approx. CableWeight (kg/km)', 'Approx. CableWeight (kg/km)') | Approx. CableDiameter (mm) | Approx. Copper Weight (kg/km) | Approx. Cable Weight (kg/km) | Mutual Capacitance | Conductor : | Insulation : | Core colours : | ('Approx. Overall Dia. (mm)', 'Approx. Overall Dia. (mm)')
https://www.rrkabel.com/control-cable/ratnaflex-multicore-694 | RATNAFLEX MULTICORE (IS 694) | ['https://www.rrkabel.com/Uploads/Products/27/ProductZoomForMoreDetailsImage/Ratna-Flex-Multicore.jpg', 'https://www.rrkabel.com/Uploads/Products/27/ProductZoomImage/Ratna-Flex-Multicore-1.jpg', 'https://www.rrkabel.com/Uploads/Products/79/ProductFeaturesDetails/1.png', 'https://www.rrkabel.com/Uploads/Products/79/ProductFeaturesDetails/1.png'] | ['These cables are designed for residential and commercial infrastructure. They serve as the connecting medium in power and control panels, cabinets & switchgears. They can also used for the purposes such as stationary and static appliances, motors and for other single phase connections.'] | ['PVC insulated & sheathed multicore cables suitable for all general purpose wirings for max. operating temperature of 70', 'o', 'C.'] | ['HR PVC insulated & sheathed multicore cables suitable for higher operating temperature of 70', 'o', 'C.'] | ['Flame Retardant (FR) multicore cable enhances safety and are suitable for max. operating temperature 70', 'o', 'C.'] | ['Heat Resistant (HR) & Flame Retardant (FR) multicore cables are suitable for higher operating temperature up to 85', 'o', 'C with enhanced safety.'] | ['IS 694 marked, FIA/TAC'] | ['Electrolytic grade annealed copper Class 5 as per IS 8130'] | ['Black, grey & white'] | ['Up to and including 1100V'] | ['Kindly add ‘OU’ after the part number, for the cables requred for outdoor application.']
[13 empty] | RATNAFLEX-M | IS 694, IS 8130 Class 5, IS 5831 Type D for insulation & ST-3 & for sheathing
[13 empty] | RATNAFLEX-M HR | IS 694, IS 8130 Class 5, IS 5831 Type C for insulation & ST-2 for sheathing
[13 empty] | RATNAFLEX-M FR | IS 694, IS 8130 Class 5, IS 5831 Type D for insulation & ST-3 (FR) & for sheathing
[13 empty] | RATNAFLEX-M HR FR | IS 694, IS 8130 Class 5, IS 5831 Type C for insulation & ST-2 (FR) for sheathing
[13 empty] | RATNAFLEX-M FR-LSH | IS 694, IS 8130 Class 5, IS 5831 Type D for insulation & ST-3 (FR-LSH) for sheathing
[15 empty] | Please complete the part numbers for these cables by adding the suffix (in place of ‘xx’) for the insulation colour required. | Kindly complete the part numbers for these cables by adding the suffix (in place of ‘y’) for the product type required. | Kindly complete the part numbers for these cables by adding the suffix (in place of ‘z’) for the sheath colour required.
[15 empty] | 06 – green-yellow earth core. We offer green/yellow earth core as our standard product. 00 – without green-yellow earth core (available on request). | 1 – PVC 70°C, 2 – PVC FR 70°C, 3 – PVC HR 85°C, 4 – PVC HR 85°C + FR, 5 – PVC FR-LSH. | 1 – black, 4 – grey, 5 – white.
[18 empty] | 03010101xxyz | 1 | 0.5 | 0.6 | 39 | 0.9 | 4.3
[18 empty] | 03010102xxyz | 2 | 0.5 | 0.6 | 39 | 0.9 | 6.9
[18 empty] | 03010103xxyz | 3 | 0.5 | 0.6 | 39 | 0.9 | 7.3
[18 empty] | 03010104xxyz | 4 | 0.5 | 0.6 | 39 | 0.9 | 8
[18 empty] | 03010105xxyz | 5 | 0.5 | 0.6 | 39 | 0.9 | 8.7
[18 empty] | 03010106xxyz | 1 | 0.75 | 0.6 | 26 | 0.9 | 4.5
[18 empty] | 03010107xxyz | 2 | 0.75 | 0.6 | 26 | 0.9 | 7.3
[18 empty] | 03010108xxyz | 3 | 0.75 | 0.6 | 26 | 0.9 | 7.7
[18 empty] | 03010109xxyz | 4 | 0.75 | 0.6 | 26 | 0.9 | 8.4
[18 empty] | 03010110xxyz | 5 | 0.75 | 0.6 | 26 | 0.9 | 9.2
[18 empty] | 03010111xxyz | 1 | 1 | 0.6 | 19.5 | 0.9 | 4.7
[18 empty] | 03010112xxyz | 2 | 1 | 0.6 | 19.5 | 0.9 | 7.6
[18 empty] | 03010113xxyz | 3 | 1 | 0.6 | 19.5 | 0.9 | 8.1
[18 empty] | 03010114xxyz | 4 | 1 | 0.6 | 19.5 | 0.9 | 8.8
[18 empty] | 03010115xxyz | 5 | 1 | 0.6 | 19.5 | 1 | 9.6
[18 empty] | 03010116xxyz | 1 | 1.5 | 0.6 | 13.3 | 0.9 | 5.4
[18 empty] | 03010117xxyz | 2 | 1.5 | 0.6 | 13.3 | 0.9 | 8.9
[18 empty] | 03010118xxyz | 3 | 1.5 | 0.6 | 13.3 | 0.9 | 9.4
[18 empty] | 03010119xxyz | 4 | 1.5 | 0.6 | 13.3 | 1 | 10.4
[18 empty] | 03010120xxyz | 5 | 1.5 | 0.6 | 13.3 | 1 | 11.4
[18 empty] | 03010121xxyz | 1 | 2.5 | 0.7 | 7.98 | 1 | 6.2
[18 empty] | 03010122xxyz | 2 | 2.5 | 0.7 | 7.98 | 1 | 10.3
[18 empty] | 03010123xxyz | 3 | 2.5 | 0.7 | 7.98 | 1 | 10.9
[18 empty] | 03010124xxyz | 4 | 2.5 | 0.7 | 7.98 | 1 | 12
[18 empty] | 03010125xxyz | 5 | 2.5 | 0.7 | 7.98 | 1 | 13.2
[18 empty] | 03010126xxyz | 1 | 4 | 0.8 | 4.95 | 1 | 6.8
[18 empty] | 03010127xxyz | 2 | 4 | 0.8 | 4.95 | 1 | 11.6
[18 empty] | 03010128xxyz | 3 | 4 | 0.8 | 4.95 | 1 | 12.4
[18 empty] | 03010129xxyz | 4 | 4 | 0.8 | 4.95 | 1 | 13.6
[18 empty] | 03010130xxyz | 5 | 4 | 0.8 | 4.95 | 1.1 | 15.3
[18 empty] | 03010131xxyz | 1 | 6 | 0.8 | 3.3 | 1.1 | 7.5
[18 empty] | 03010132xxyz | 2 | 6 | 0.8 | 3.3 | 1.1 | 13
[18 empty] | 03010133xxyz | 3 | 6 | 0.8 | 3.3 | 1.2 | 13.8
[18 empty] | 03010134xxyz | 4 | 6 | 0.8 | 3.3 | 1.2 | 15.5
[18 empty] | 03010135xxyz | 1 | 10 | 1 | 1.91 | 1.3 | 9.4
[18 empty] | 03010136xxyz | 2 | 10 | 1 | 1.91 | 1.3 | 16.5
[18 empty] | 03010137xxyz | 3 | 10 | 1 | 1.91 | 1.4 | 17.7
[18 empty] | 03010138xxyz | 4 | 10 | 1 | 1.91 | 1.4 | 19.5
[18 empty] | 03010139xxyz | 1 | 16 | 1 | 1.21 | 1.4 | 10.9
[18 empty] | 03010140xxyz | 2 | 16 | 1 | 1.21 | 1.4 | 19.4
[18 empty] | 03010141xxyz | 3 | 16 | 1 | 1.21 | 1.4 | 20.6
[18 empty] | 03010142xxyz | 4 | 16 | 1 | 1.21 | 1.4 | 23
[18 empty] | 03010143xxyz | 1 | 25 | 1.2 | 0.78 | 1.4 | 13.6
[18 empty] | 03010144xxyz | 2 | 25 | 1.2 | 0.78 | 1.4 | 23.8
[18 empty] | 03010145xxyz | 3 | 25 | 1.2 | 0.78 | 1.5 | 25.6
[18 empty] | 03010146xxyz | 4 | 25 | 1.2 | 0.78 | 1.6 | 28.5
[18 empty] | 03010147xxyz | 1 | 35 | 1.2 | 0.554 | 1.6 | 15.5
[18 empty] | 03010148xxyz | 2 | 35 | 1.2 | 0.554 | 1.6 | 27.2
[18 empty] | 03010149xxyz | 3 | 35 | 1.2 | 0.554 | 1.6 | 29.3
[18 empty] | 03010150xxyz | 4 | 35 | 1.2 | 0.554 | 1.7 | 32.7
[18 empty] | 03010151xxyz | 1 | 50 | 1.4 | 0.386 | 2 | 18.1
[18 empty] | 03010152xxyz | 2 | 50 | 1.4 | 0.386 | 2 | 32
[18 empty] | 03010153xxyz | 3 | 50 | 1.4 | 0.386 | 2 | 34.6
[18 empty] | 03010154xxyz | 4 | 50 | 1.4 | 0.386 | 2 | 38.6
[18 empty] | 03010155xxyz | 1 | 70 | 1.4 | 0.272 | 2.2 | 20.8
[18 empty] | 03010156xxyz | 2 | 70 | 1.4 | 0.272 | 2.2 | 36.8
[18 empty] | 03010157xxyz | 3 | 70 | 1.4 | 0.272 | 2.2 | 39.6
[18 empty] | 03010158xxyz | 4 | 70 | 1.4 | 0.272 | 2.2 | 44.3
[18 empty] | 03010159xxyz | 1 | 95 | 1.6 | 0.206 | 2.4 | 23.6
[18 empty] | 03010160xxyz | 2 | 95 | 1.6 | 0.206 | 2.4 | 41.8
[18 empty] | 03010161xxyz | 3 | 95 | 1.6 | 0.206 | 2.4 | 47
[18 empty] | 03010162xxyz | 4 | 95 | 1.6 | 0.206 | 2.4 | 50.2
[18 empty] | 03010163xxyz | 1 | 120 | 1.6 | 0.161 | 2.5 | 26
[18 empty] | 03010164xxyz | 2 | 120 | 1.6 | 0.161 | 2.5 | 46.2
[18 empty] | 03010165xxyz | 3 | 120 | 1.6 | 0.161 | 2.5 | 51
[18 empty] | 03010166xxyz | 4 | 120 | 1.6 | 0.161 | 2.5 | 55.7
[18 empty] | 03010167xxyz | 3 | 150 | 1.8 | 0.129 | 2.6 | 54.8
[18 empty] | 03010168xxyz | 4 | 150 | 1.8 | 0.129 | 2.6 | 62.1
[18 empty] | 03010169xxyz | 3 | 185 | 2 | 0.106 | 2.8 | 61.2
[18 empty] | 03010170xxyz | 4 | 185 | 2 | 0.106 | 2.8 | 68.5
[18 empty] | 03010171xxyz | 3 | 240 | 2.2 | 0.0801 | 3 | 69.7
[18 empty] | 03010172xxyz | 4 | 240 | 2.2 | 0.0801 | 3 | 77.9
[18 empty] | 03010173xxyz | 3 | 300 | 2.4 | 0.0641 | 3.2 | 75.7
[18 empty] | 03010174xxyz | 4 | 300 | 2.4 | 0.0641 | 3.2 | 84.4
https://www.rrkabel.com/ProductsDetails/index/175 | Control Cables (IS 694) | ['https://www.rrkabel.com/Uploads/Products/175/ProductZoomForMoreDetailsImage/ControlCables_CSIS694.png', 'https://www.rrkabel.com/Uploads/Products/175/ProductZoomImage/ControlCablewithnameIS694.jpg', 'https://www.rrkabel.com/Uploads/Products/494/ProductFeaturesDetails/ControlCablesIS694.png', 'https://www.rrkabel.com/Uploads/Products/494/ProductFeaturesDetails/ControlCablesIS694.png'] |  | ['PVC insulated & sheathed multicore cables suitable for all general purpose wirings for max. operating temperature of 70oC.'] | ['HR PVC insulated & sheathed multicore cales suitable for higher operating temperature of 70oC.'] | ['Flame Retardant (FR) multicore cable enhances safety and are suitable for max. operating temperature 70oC.'] | ['Heat Resistant (HR) & Flame Retardant (FR) multicore cables are suitable for higher operating temperature up to 85oC with enhanced safety.'] |  |  |  |  | ["Kindly add 'OU' after the part number, for the cables required for outdoor application."] | [12 empty] | ['These cables are designed for residential and commercial infrastructure. They serve as the connecting medium in power and control panels, cabinets & switchgears. They can also used for the purposes such as stationary and static appliances, motors and for other single phase connections.'] | ['Approvals : IS 694 marked, FIA/TAC Conductor : Electrolytic grade annealed copper Class-5 as per IS 8130, having uniform resistance properties Core Colours:All black colour cores with continuous white numbering, gn-yl core on outer most layer for earth if applicable Standard Cable Colour :Black (RAL 9005) & Grey (RAL 7001) Voltage : Up to and including 1100V Packing : Standard packing of 100 mtr. in coils. Longer length available on requests']
[14 empty] | IS 694, IS 8130 Class 5, IS 5831 Type D for insulation & ST-3 & for sheathing | [12 empty] | PVC 70°C
[14 empty] | IS 694, IS 8130 Class 5, IS 5831 Type C for insulation & ST-2 for sheathing | [12 empty] | Heat Resistant 85°C
[14 empty] | IS 694, IS 8130 Class 5, IS 5831 Type D for insulation & ST-3 (FR) & for sheathing | [12 empty] | Flame Retardant
[14 empty] | IS 694, IS 8130 Class 5, IS 5831 Type C for insulation & ST-2 (FR) for sheathing | [12 empty] | Heat Resistant 85°C & Flame Retardant
[14 empty] | IS 694, IS 8130 Class 5, IS 5831 Type D for insulation & ST-3 (FR-LSH) for sheathing | [12 empty] | Flame Retardant Low Smoke Low Halogen
[15 empty] | Please complete the part numbers for these cables by adding the suffix (in place of 'xx') for the insulation colour required. | Kindly complete the part numbers for these cables by adding the suffix (in place of 'y') for the product type required. | Kindly complete the part numbers for these cables by adding the suffix (in place of 'z') for the sheath colour required.
[15 empty] | 06 - green-yellow earth core. We offer green/yellow earth core as our standard product. 00 - without green-yellow earth core (available on request). | 1 - PVC 70°C, 2 - PVC FR 70°C, 3 - PVC HR 85°C, 4 - PVC HR 85°C + FR, 5 - PVC FR-LSH 70°C. | 1 - black, 4 - grey.
[18 empty] | 03020101xxyz | 6 |  |  |  |  | 9.5 |  |  |  | 0.5 | 0.6 | 0.9
[18 empty] | 03020102xxyz | 7 |  |  |  |  | 9.5 |  |  |  | 0.5 | 0.6 | 0.9
[18 empty] | 03020103xxyz | 8 |  |  |  |  | 11.1 |  |  |  | 0.5 | 0.6 | 1
[18 empty] | 03020104xxyz | 9 |  |  |  |  | 11.8 |  |  |  | 0.5 | 0.6 | 1
[18 empty] | 03020105xxyz | 10 |  |  |  |  | 12 |  |  |  | 0.5 | 0.6 | 1
[18 empty] | 03020106xxyz | 11 |  |  |  |  | 12 |  |  |  | 0.5 | 0.6 | 1
[18 empty] | 03020107xxyz | 12 |  |  |  |  | 12.4 |  |  |  | 0.5 | 0.6 | 1
[18 empty] | 03020108xxyz | 13 |  |  |  |  | 13.1 |  |  |  | 0.5 | 0.6 | 1
[18 empty] | 03020109xxyz | 14 |  |  |  |  | 13.1 |  |  |  | 0.5 | 0.6 | 1.1
[18 empty] | 03020110xxyz | 15 |  |  |  |  | 13.5 |  |  |  | 0.5 | 0.6 | 1.1
[18 empty] | 03020111xxyz | 16 |  |  |  |  | 13.8 |  |  |  | 0.5 | 0.6 | 1.1
[18 empty] | 03020112xxyz | 17 |  |  |  |  | 14.6 |  |  |  | 0.5 | 0.6 | 1.1
[18 empty] | 03020113xxyz | 18 |  |  |  |  | 14.6 |  |  |  | 0.5 | 0.6 | 1.1
[18 empty] | 03020114xxyz | 19 |  |  |  |  | 14.6 |  |  |  | 0.5 | 0.6 | 1.1
[18 empty] | 03020115xxyz | 20 |  |  |  |  | 15.4 |  |  |  | 0.5 | 0.6 | 1.2
[18 empty] | 03020116xxyz | 21 |  |  |  |  | 15.4 |  |  |  | 0.5 | 0.6 | 1.2
[18 empty] | 03020117xxyz | 22 |  |  |  |  | 16.3 |  |  |  | 0.5 | 0.6 | 1.2
[18 empty] | 03020118xxyz | 23 |  |  |  |  | 16.3 |  |  |  | 0.5 | 0.6 | 1.2
[18 empty] | 03020119xxyz | 24 |  |  |  |  | 17.1 |  |  |  | 0.5 | 0.6 | 1.2
[18 empty] | 03020120xxyz | 25 |  |  |  |  | 17.1 |  |  |  | 0.5 | 0.6 | 1.2
[18 empty] | 03020121xxyz | 6 |  |  |  |  | 10 |  |  |  | 0.75 | 0.6 | 1
[18 empty] | 03020122xxyz | 7 |  |  |  |  | 10 |  |  |  | 0.75 | 0.6 | 1
[18 empty] | 03020123xxyz | 8 |  |  |  |  | 11.8 |  |  |  | 0.75 | 0.6 | 1
[18 empty] | 03020124xxyz | 9 |  |  |  |  | 12.4 |  |  |  | 0.75 | 0.6 | 1.1
[18 empty] | 03020125xxyz | 10 |  |  |  |  | 12.7 |  |  |  | 0.75 | 0.6 | 1.1
[18 empty] | 03020126xxyz | 11 |  |  |  |  | 12.7 |  |  |  | 0.75 | 0.6 | 1.1
[18 empty] | 03020127xxyz | 12 |  |  |  |  | 13.1 |  |  |  | 0.75 | 0.6 | 1.1
[18 empty] | 03020128xxyz | 13 |  |  |  |  | 13.8 |  |  |  | 0.75 | 0.6 | 1.1
[18 empty] | 03020129xxyz | 14 |  |  |  |  | 13.8 |  |  |  | 0.75 | 0.6 | 1.1
[18 empty] | 03020130xxyz | 15 |  |  |  |  | 14.3 |  |  |  | 0.75 | 0.6 | 1.2
[18 empty] | 03020131xxyz | 16 |  |  |  |  | 14.6 |  |  |  | 0.75 | 0.6 | 1.2
[18 empty] | 03020132xxyz | 17 |  |  |  |  | 15.4 |  |  |  | 0.75 | 0.6 | 1.2
[18 empty] | 03020133xxyz | 18 |  |  |  |  | 15.4 |  |  |  | 0.75 | 0.6 | 1.2
[18 empty] | 03020134xxyz | 19 |  |  |  |  | 15.4 |  |  |  | 0.75 | 0.6 | 1.2
[18 empty] | 03020135xxyz | 20 |  |  |  |  | 16.3 |  |  |  | 0.75 | 0.6 | 1.3
[18 empty] | 03020136xxyz | 21 |  |  |  |  | 16.3 |  |  |  | 0.75 | 0.6 | 1.3
[18 empty] | 03020137xxyz | 22 |  |  |  |  | 17.3 |  |  |  | 0.75 | 0.6 | 1.3
[18 empty] | 03020138xxyz | 23 |  |  |  |  | 17.3 |  |  |  | 0.75 | 0.6 | 1.3
[18 empty] | 03020139xxyz | 24 |  |  |  |  | 18.2 |  |  |  | 0.75 | 0.6 | 1.3
[18 empty] | 03020140xxyz | 25 |  |  |  |  | 19 |  |  |  | 0.75 | 0.6 | 1.2
[18 empty] | 03020141xxyz | 6 |  |  |  |  | 10.5 |  |  |  | 1 | 0.6 | 1
[18 empty] | 03020142xxyz | 7 |  |  |  |  | 10.5 |  |  |  | 1 | 0.6 | 1
[18 empty] | 03020143xxyz | 8 |  |  |  |  | 12.4 |  |  |  | 1 | 0.6 | 1
[18 empty] | 03020144xxyz | 9 |  |  |  |  | 13.1 |  |  |  | 1 | 0.6 | 1.1
[18 empty] | 03020145xxyz | 10 |  |  |  |  | 13.4 |  |  |  | 1 | 0.6 | 1.1
[18 empty] | 03020146xxyz | 11 |  |  |  |  | 13.4 |  |  |  | 1 | 0.6 | 1.1
[18 empty] | 03020147xxyz | 12 |  |  |  |  | 13.9 |  |  |  | 1 | 0.6 | 1.1
[18 empty] | 03020148xxyz | 13 |  |  |  |  | 14.6 |  |  |  | 1 | 0.6 | 1.1
[18 empty] | 03020149xxyz | 14 |  |  |  |  | 14.6 |  |  |  | 1 | 0.6 | 1.1
[18 empty] | 03020150xxyz | 15 |  |  |  |  | 15.1 |  |  |  | 1 | 0.6 | 1.2
[18 empty] | 03020151xxyz | 16 |  |  |  |  | 15.4 |  |  |  | 1 | 0.6 | 1.2
[18 empty] | 03020152xxyz | 17 |  |  |  |  | 16.3 |  |  |  | 1 | 0.6 | 1.2
[18 empty] | 03020153xxyz | 18 |  |  |  |  | 16.3 |  |  |  | 1 | 0.6 | 1.3
[18 empty] | 03020154xxyz | 19 |  |  |  |  | 16.3 |  |  |  | 1 | 0.6 | 1.3
[18 empty] | 03020155xxyz | 20 |  |  |  |  | 17.3 |  |  |  | 1 | 0.6 | 1.4
[18 empty] | 03020156xxyz | 21 |  |  |  |  | 17.3 |  |  |  | 1 | 0.6 | 1.4
[18 empty] | 03020157xxyz | 22 |  |  |  |  | 18.2 |  |  |  | 1 | 0.6 | 1.4
[18 empty] | 03020158xxyz | 23 |  |  |  |  | 18.2 |  |  |  | 1 | 0.6 | 1.4
[18 empty] | 03020159xxyz | 24 |  |  |  |  | 19.2 |  |  |  | 1 | 0.6 | 1.4
[18 empty] | 03020160xxyz | 25 |  |  |  |  | 19.2 |  |  |  | 1 | 0.6 | 1.4
[18 empty] | 03020161xxyz | 6 |  |  |  |  | 12.4 |  |  |  | 1.5 | 0.6 | 1
[18 empty] | 03020162xxyz | 7 |  |  |  |  | 12.4 |  |  |  | 1.5 | 0.6 | 1
[18 empty] | 03020163xxyz | 8 |  |  |  |  | 14.7 |  |  |  | 1.5 | 0.6 | 1.1
[18 empty] | 03020164xxyz | 9 |  |  |  |  | 15.6 |  |  |  | 1.5 | 0.6 | 1.1
[18 empty] | 03020165xxyz | 10 |  |  |  |  | 16 |  |  |  | 1.5 | 0.6 | 1.1
[18 empty] | 03020166xxyz | 11 |  |  |  |  | 16 |  |  |  | 1.5 | 0.6 | 1.1
[18 empty] | 03020167xxyz | 12 |  |  |  |  | 16.5 |  |  |  | 1.5 | 0.6 | 1.1
[18 empty] | 03020168xxyz | 13 |  |  |  |  | 17.4 |  |  |  | 1.5 | 0.6 | 1.2
[18 empty] | 03020169xxyz | 14 |  |  |  |  | 17.4 |  |  |  | 1.5 | 0.6 | 1.2
[18 empty] | 03020170xxyz | 15 |  |  |  |  | 18.1 |  |  |  | 1.5 | 0.6 | 1.2
[18 empty] | 03020171xxyz | 16 |  |  |  |  | 18.4 |  |  |  | 1.5 | 0.6 | 1.2
[18 empty] | 03020172xxyz | 17 |  |  |  |  | 19.5 |  |  |  | 1.5 | 0.6 | 1.3
[18 empty] | 03020173xxyz | 18 |  |  |  |  | 19.5 |  |  |  | 1.5 | 0.6 | 1.3
[18 empty] | 03020174xxyz | 19 |  |  |  |  | 19.5 |  |  |  | 1.5 | 0.6 | 1.3
[18 empty] | 03020175xxyz | 20 |  |  |  |  | 20.7 |  |  |  | 1.5 | 0.6 | 1.4
[18 empty] | 03020176xxyz | 21 |  |  |  |  | 20.7 |  |  |  | 1.5 | 0.6 | 1.4
[18 empty] | 03020177xxyz | 22 |  |  |  |  | 21.9 |  |  |  | 1.5 | 0.6 | 1.4
[18 empty] | 03020178xxyz | 23 |  |  |  |  | 21.9 |  |  |  | 1.5 | 0.6 | 1.4
[18 empty] | 03020179xxyz | 24 |  |  |  |  | 23 |  |  |  | 1.5 | 0.6 | 1.4
[18 empty] | 03020180xxyz | 25 |  |  |  |  | 23 |  |  |  | 1.5 | 0.6 | 1.4
[18 empty] | 03020181xxyz | 6 |  |  |  |  | 14.5 |  |  |  | 2.5 | 0.7 | 1.1
[18 empty] | 03020182xxyz | 7 |  |  |  |  | 15.5 |  |  |  | 2.5 | 0.7 | 1.1
[18 empty] | 03020183xxyz | 8 |  |  |  |  | 17.3 |  |  |  | 2.5 | 0.7 | 1.2
[18 empty] | 03020184xxyz | 9 |  |  |  |  | 18.3 |  |  |  | 2.5 | 0.7 | 1.3
[18 empty] | 03020185xxyz | 10 |  |  |  |  | 18.7 |  |  |  | 2.5 | 0.7 | 1.3
[18 empty] | 03020186xxyz | 11 |  |  |  |  | 18.7 |  |  |  | 2.5 | 0.7 | 1.3
[18 empty] | 03020187xxyz | 12 |  |  |  |  | 19.4 |  |  |  | 2.5 | 0.7 | 1.3
[18 empty] | 03020188xxyz | 13 |  |  |  |  | 20.5 |  |  |  | 2.5 | 0.7 | 1.3
[18 empty] | 03020189xxyz | 14 |  |  |  |  | 20.5 |  |  |  | 2.5 | 0.7 | 1.3
[18 empty] | 03020190xxyz | 15 |  |  |  |  | 21.3 |  |  |  | 2.5 | 0.7 | 1.4
[18 empty] | 03020191xxyz | 16 |  |  |  |  | 21.7 |  |  |  | 2.5 | 0.7 | 1.4
[18 empty] | 03020192xxyz | 17 |  |  |  |  | 23 |  |  |  | 2.5 | 0.7 | 1.4
[18 empty] | 03020193xxyz | 18 |  |  |  |  | 23.3 |  |  |  | 2.5 | 0.7 | 1.4
[18 empty] | 03020194xxyz | 19 |  |  |  |  | 23.8 |  |  |  | 2.5 | 0.7 | 1.4
[18 empty] | 03020195xxyz | 20 |  |  |  |  | 24.4 |  |  |  | 2.5 | 0.7 | 1.4
[18 empty] | 03020196xxyz | 21 |  |  |  |  | 25 |  |  |  | 2.5 | 0.7 | 1.5
[18 empty] | 03020197xxyz | 22 |  |  |  |  | 25.8 |  |  |  | 2.5 | 0.7 | 1.5
[18 empty] | 03020198xxyz | 23 |  |  |  |  | 26.3 |  |  |  | 2.5 | 0.7 | 1.5
[18 empty] | 03020199xxyz | 24 |  |  |  |  | 27.2 |  |  |  | 2.5 | 0.7 | 1.5
[18 empty] | 03020200xxyz | 25 |  |  |  |  | 27.9 |  |  |  | 2.5 | 0.7 | 1.5
https://www.rrkabel.com/control-cable/control-cable-h05vvh2 | H03/H05VVH2-F & H03/H05VV-F | ['https://www.rrkabel.com/Uploads/Products/29/ProductZoomForMoreDetailsImage/JB-500.jpg', 'https://www.rrkabel.com/Uploads/Products/29/ProductZoomImage/JB-500-1.jpg', 'https://www.rrkabel.com/Uploads/Products/85/ProductFeaturesDetails/H03H05VVH2-F H03H05VV-F.png', 'https://www.rrkabel.com/Uploads/Products/85/ProductFeaturesDetails/H03H05VVH2-F H03H05VV-F.png'] | [22 empty] | ['For use in connections of household appliances, plant and machinery, wiring purposes and for manufacturing cords.'] | [5 empty] | ['BS EN 50525-2-11, DIN EN 50525-2-11; VDE 0285-525-2-11, EN 50525-2-11.'] | ['300/500V (H05VV-F & H05VVH2-F); 300/300V (H03VV-F & H03VVH2-F)'] | ['Min. 20 GΩ x cm'] | ['Flexing -5°C to +70°C. Fixed Installation : -30°C to +70°C'] | ['Flexing 7.5 x cable ø; Fixed installation 4 x cable ø'] | ['4000V'] | ['Bare copper, fine wire conductors, as per EN 60228 Cl.5. PVC core insulation TI2, to EN 50363-3.Harmonised core colour to HD 308 (Refer Appendix Table No. 1-1). Cores stranded in layers with optimal lay-length.PVC outer sheath TM2, to EN 50363-4.1.', 'H05VV-F is also available in oil resistant variant as H05VV5-F.The outer sheath provided here is of special PVC, TM5 to BS EN 50363-4.1.'] | ['PVC self-extinguishing and flame retardant according to EN 60332-1-2.Please complete the part numbers for these cables by adding the suffix (in place of "z") for the sheath colour required:1 - black (RAL 9005), 3 - grey (RAL 7001), 5 - white (RAL 9010). For Oil Resistant sheath kindly add "OR" after the part nos.'] | ['Note : *G = With green/yellow earth core X = Without green/yellow earth core']
H03VV-F
[40 empty] | H03VV-F | 03030101021z | 2 x 0.5 | 5.1
[40 empty] | H03VV-F | 03030102021z | 2 x 0.75 | 5.5
[40 empty] | H03VV-F | 03030103021z | 3 x 0.5 | 5.3
[40 empty] | H03VV-F | 03030104011z | 3 G 0.5 | 5.3
[40 empty] | H03VV-F | 03030105021z | 3 x 0.75 | 5.7
[40 empty] | H03VV-F | 03030106011z | 3 G 0.75 | 5.7
[41 empty] | 03030107021z | 4 x 0.5 | 5.8
[41 empty] | 03030109021z | 4 x 0.75 | 6.3
[41 empty] | 03030110011z | 4 G 0.75 | 6.3
[40 empty] | H03VVH2-F | 03031111021z | 2 x 0.5 | 5.1 x 3.2
[40 empty] | H03VVH2-F | 03031112021z | 2 x 0.75 | 5.5 x 3.4
[40 empty] | H05VVH2-F | 03031113021z | 2 x 0.75 | 6.3 x 4.0
[40 empty] | H05VVH2-F | 03031114021z | 2 x 1 | 6.6 x 4.1
[40 empty] | H05VVH2-F | 03031115021z | 2 x 1.5 | 7.7 x 4.7
[40 empty] | H05VV-F | 03030116021z | 2 x 0.75 | 6.2
[40 empty] | H05VV-F | 03030117021z | 2 x 1 | 6.4
[40 empty] | H05VV-F | 03030118021z | 2 x 1.5 | 7.5
[40 empty] | H05VV-F | 03030119021z | 2 x 2.5 | 9.1
[40 empty] | H05VV-F | 03030120021z | 2 x 4 | 10.3
[40 empty] | H05VV-F | 03030121011z | 3 G 0.75 | 6.6
[40 empty] | H05VV-F | 03030122021z | 3 x 0.75 | 6.6
[40 empty] | H05VV-F | 03030123011z | 3 G 1 | 6.9
[40 empty] | H05VV-F | 03030124021z | 3 x 1 | 6.9
[40 empty] | H05VV-F | 03030125011z | 3 G 1.5 | 8.1
[40 empty] | H05VV-F | 03030126021z | 3 x 1.5 | 8.1
[40 empty] | H05VV-F | 03030127011z | 3 G 2.5 | 9.7
[40 empty] | H05VV-F | 03030128021z | 3 x 2.5 | 9.7
[40 empty] | H05VV-F | 03030129011z | 3 G 4 | 11.2
[40 empty] | H05VV-F | 03030130021z | 3 x 4 | 11.2
[40 empty] | H05VV-F | 03030131011z | 4 G 0.75 | 7.1
[40 empty] | H05VV-F | 03030132021z | 4 x 0.75 | 7.1
[40 empty] | H05VV-F | 03030133011z | 4 G 1 | 7.5
[40 empty] | H05VV-F | 03030134021z | 4 x 1 | 7.5
[40 empty] | H05VV-F | 03030135011z | 4 G 1.5 | 9.1
[40 empty] | H05VV-F | 03030136021z | 4 x 1.5 | 9.1
[40 empty] | H05VV-F | 03030137011z | 4 G 2.5 | 10.7
[40 empty] | H05VV-F | 03030138021z | 4 x 2.5 | 10.7
[40 empty] | H05VV-F | 03030139011z | 4 G 4 | 12.2
[40 empty] | H05VV-F | 03030140021z | 4 x 4 | 12.2
[40 empty] | H05VV-F | 03030141011z | 5 G 0.75 | 8.0
[40 empty] | H05VV-F | 03030142021z | 5 x 0.75 | 8.0
[40 empty] | H05VV-F | 03030143011z | 5 G 1 | 8.4
[40 empty] | H05VV-F | 03030144021z | 5 x 1 | 8.4
[41 empty] | 03030146021z | 5 x 1.5 | 10.2
[41 empty] | 03030147011z | 5 G 2.5 | 12.0
[41 empty] | 03030148021z | 5 x 2.5 | 12.0
[41 empty] | 03030149011z | 5 G 4 | 13.8
[41 empty] | 03030150021z | 5 x 4 | 13.8
[45 empty] | H03VVH2-F | – | 0.50…0.75 mm² x 2C
[45 empty] | H05VVH2-F | 0.75 . . . . 1.5 mm² x 2C | 0.75…1 mm² x 2C
[45 empty] | H05VV-F | 0.75…4 mm² x 2…5C | 0.75…4 mm² x 2…5C
https://www.rrkabel.com/ProductsDetails/index/174 | JB-750 | ['https://www.rrkabel.com/Uploads/Products/174/ProductZoomForMoreDetailsImage/JB-750_CS.png', 'https://www.rrkabel.com/Uploads/Products/174/ProductZoomImage/JB-750_CSwithname.jpg', 'https://www.rrkabel.com/Uploads/Products/493/ProductFeaturesDetails/JB-750.png', 'https://www.rrkabel.com/Uploads/Products/493/ProductFeaturesDetails/JB-750.png'] | [22 empty] | ['For use in connections of household appliances and wiring purposes. It is also used in manufacture of cords.'] | ['Nominal Voltage : U0 / U 450 / 750V Insulation Resistance : Min. 20 GΩ x cm Temperature Range : Flexing -5°C to +70°C. Fixed installation -30°C to +70°C Minimum Bending Radius : Flexing 7.5 x cable ø. Fixed installation 4 x cable ø Test Voltage : 4000V Breakdown Voltage : Min. 8000V'] |  |  |  |  | ['Adapted to DIN VDE 0281, 0293, 0295 with insulation thickness for 1.0 kV type.'] | [5 empty] | ['Bare copper, fine wire conductors, as per EN60228 Cl. 5. Special PVC core insulation TI2, to EN 50363-3. Harmonised core colour to HD 308 (Refer Appendix Table No. 1-1). For cores above 5, black core with continuous white numbering according to DIN VDE 0293. Green/yellow earth core in outer layer (3 cores and above). Cores stranded in layers with optimal lay-length. Special PVC outer sheath TM2, to EN 50363-4-1. Colour Grey (RAL 7001).'] | ['PVC self-extinguishing and flame retardant according to EN 60332-1-2.']
[18 empty] | 30400201205 | [30 empty] | 2 x 2.5 | 9.1
[18 empty] | 30400311205 | [30 empty] | 3G 2.5 | 9.9
[18 empty] | 30400301205 | [30 empty] | 3 x 2.5 | 9.9
[18 empty] | 30400411205 | [30 empty] | 4G 2.5 | 11.1
[18 empty] | 30400401205 | [30 empty] | 4 x 2.5 | 11.1
[18 empty] | 30400511205 | [30 empty] | 5G 2.5 | 12.4
[18 empty] | 30400501205 | [30 empty] | 5 x 2.5 | 12.4
[18 empty] | 30400611205 | [30 empty] | 6G 2.5 | 13.3
[18 empty] | 30400711205 | [30 empty] | 7G 2.5 | 14.6
[18 empty] | 30400200004 | [30 empty] | 2 x 4 | 10.4
[18 empty] | 30400310004 | [30 empty] | 3G 4 | 11.2
[18 empty] | 30400410004 | [30 empty] | 4G 4 | 12.5
[18 empty] | 30400510004 | [30 empty] | 5G 4 | 13.9
[18 empty] | 30400710004 | [30 empty] | 7G 4 | 16.8
[18 empty] | 30401110004 | [30 empty] | 11G 4 | 22.3
[18 empty] | 30400310006 | [30 empty] | 3G 6 | 12.6
[18 empty] | 30400410006 | [30 empty] | 4G 6 | 14
[18 empty] | 30400510006 | [30 empty] | 5G 6 | 15.5
[18 empty] | 30400710006 | [30 empty] | 7G 6 | 19
[18 empty] | 30400310010 | [30 empty] | 3G 10 | 16
[18 empty] | 30400410010 | [30 empty] | 4G 10 | 18
[18 empty] | 30400510010 | [30 empty] | 5G 10 | 20
[18 empty] | 30400710010 | [30 empty] | 7G 10 | 23.1
[18 empty] | 30400310016 | [30 empty] | 3G 16 | 18.5
[18 empty] | 30400410016 | [30 empty] | 4G 16 | 20.8
[18 empty] | 30400510016 | [30 empty] | 5G 16 | 23
[18 empty] | 30400710016 | [30 empty] | 7G 16 | 31
[18 empty] | 30400310025 | [30 empty] | 3G 25 | 23.3
[18 empty] | 30400410025 | [30 empty] | 4G 25 | 26
[18 empty] | 30400510025 | [30 empty] | 5G 25 | 29
[18 empty] | 30400310035 | [30 empty] | 3G 35 | 26.6
[18 empty] | 30400410035 | [30 empty] | 4G 35 | 29.7
[18 empty] | 30400510035 | [30 empty] | 5G 35 | 33.1
[18 empty] | 30400310050 | [30 empty] | 3G 50 | 30.2
[18 empty] | 30400410050 | [30 empty] | 4G 50 | 33.9
[18 empty] | 31300411205 | [30 empty] | 5G 50 | 37.6
[18 empty] | 30400310070 | [30 empty] | 3G 70 | 37.1
[18 empty] | 30400410070 | [30 empty] | 4G 70 | 41.6
[18 empty] | 31301211205 | [30 empty] | 5G 70 | 46.3
[18 empty] | 30400310095 | [30 empty] | 3G 95 | 40.1
[18 empty] | 30400410095 | [30 empty] | 4G 95 | 44.8
[18 empty] | 30400510095 | [30 empty] | 5G 95 | 50.2
[18 empty] | 30400310120 | [30 empty] | 3G 120 | 45.5
[18 empty] | 30400410120 | [30 empty] | 4G 120 | 50.8
[18 empty] | 30400410150 | [30 empty] | 4G 150 | 57
[18 empty] | 30400410185 | [30 empty] | 4G 185 | 65.8
https://www.rrkabel.com/control-cable/control-cable-h05v2v2h2 | H03 / H05V2V2H2-F & H03 / H05V2V2-F | ['https://www.rrkabel.com/Uploads/Products/31/ProductZoomForMoreDetailsImage/H05V2V2-F-02.png', 'https://www.rrkabel.com/Uploads/Products/31/ProductZoomImage/H05V2V2-F-03.png', 'https://www.rrkabel.com/Uploads/Products/91/ProductFeaturesDetails/H05V2V2-F-01.png', 'https://www.rrkabel.com/Uploads/Products/91/ProductFeaturesDetails/H05V2V2-F-01.png'] | [22 empty] | ['For use in connections of household appliances and internal wiring purposes with high ambient temperatures and humid spaces'] | [5 empty] | ['BS EN 50525-2-11.'] | ['300 / 500V (H05V2V2H2-F / H05V2V2-F); 300 / 300V (H03V2V2H2-F / H03V2V2-F)'] | ['Min. 20 GΩ x cm'] | ['Flexing -5°C to +90°C', 'Fixed Installation -30°C to +90°C', 'Fixed Installation 5 x cable ø'] |  | ['4000V'] | ['Bare copper, fine wire conductors, as per EN 60228 Cl.5. PVC core insulation TI3, to EN 50363-3. Harmonised core colour to HD 308 (Refer Appendix Table No. 1-1). Cores stranded in layers with optimal lay-length. PVC outer sheath TM3, to EN 50363-4.1'] | ['PVC self-extinguishing and flame retardant according to EN 60332-1-2.'] | [12 empty] | ['Flexing 7.5 x cable ø; Fixed installation 4 x cable ø']
[18 empty] | 03050101001z | [30 empty] | 2 x 0.5 | 5.1 |  | H03V2V2-F
[18 empty] | 03050102001z | [30 empty] | 2 x 0.75 | 5.5 |  | H03V2V2-F
[18 empty] | 03050103001z | [30 empty] | 3 x 0.5 | 5.3 |  | H03V2V2-F
[18 empty] | 03050104001z | [30 empty] | 3 G 0.5 | 5.3 |  | H03V2V2-F
[18 empty] | 03050105001z | [30 empty] | 3 x 0.75 | 5.7 |  | H03V2V2-F
[18 empty] | 03050106001z | [30 empty] | 3 G 0.75 | 5.7 |  | H03V2V2-F
[18 empty] | 03050107001z | [30 empty] | 4 x 0.5 | 5.8 |  | H03V2V2-F
[18 empty] | 03050108001z | [30 empty] | 4 G 0.5 | 5.8 |  | H03V2V2-F
[18 empty] | 03050109001z | [30 empty] | 4 x 0.75 | 6.3 |  | H03V2V2-F
[18 empty] | 03050110001z | [30 empty] | 4 G 0.75 | 6.3 |  | H03V2V2-F
[18 empty] | 03050111001z | [30 empty] | 2 x 0.5 | 5.1 X 3.2 |  | H05V2V2H2-F
[18 empty] | 03050112001z | [30 empty] | 2 x 0.75 | 5.5 X 3.4 |  | H05V2V2H2-F
[18 empty] | 03050113001z | [30 empty] | 2 x 0.75 | 6.3 X 4.0 |  | H05V2V2H2-F
[18 empty] | 03050114001z | [30 empty] | 2 x 1.0 | 6.6 X 4.1 |  | H05V2V2H2-F
[18 empty] | 03050115001z | [30 empty] | 2 x 1.5 | 7.7 x 4.7 |  | H05V2V2H2-F
[18 empty] | 03050116001z | [30 empty] | 2 x 0.75 | 6.2 |  | H05V2V2-F
[18 empty] | 03050117001z | [30 empty] | 2 x 1.0 | 6.5 |  | H05V2V2-F
[18 empty] | 03050118001z | [30 empty] | 2 x 1.5 | 7.5 |  | H05V2V2-F
[18 empty] | 03050119001z | [30 empty] | 2 x 2.5 | 9.1 |  | H05V2V2-F
[18 empty] | 03050120001z | [30 empty] | 2 x 4 | 10.3 |  | H05V2V2-F
[18 empty] | 03050121001z | [30 empty] | 3 x 0.75 | 6.6 |  | H05V2V2-F
[18 empty] | 03050122001z | [30 empty] | 3 G 0.75 | 6.6 |  | H05V2V2-F
[18 empty] | 03050123001z | [30 empty] | 3 x 1.0 | 6.9 |  | H05V2V2-F
[18 empty] | 03050124001z | [30 empty] | 3 G 1.0 | 6.9 |  | H05V2V2-F
[18 empty] | 03050125001z | [30 empty] | 3 x 1.5 | 8.1 |  | H05V2V2-F
[18 empty] | 03050126001z | [30 empty] | 3 G 1.5 | 8.1 |  | H05V2V2-F
[18 empty] | 03050127001z | [30 empty] | 3 x 2.5 | 9.9 |  | H05V2V2-F
[18 empty] | 03050128001z | [30 empty] | 3 G 2.5 | 9.9 |  | H05V2V2-F
[18 empty] | 03050129001z | [30 empty] | 3 x 4 | 11.2 |  | H05V2V2-F
[18 empty] | 03050130001z | [30 empty] | 3 G 4 | 11.2 |  | H05V2V2-F
[18 empty] | 03050131001z | [30 empty] | 4 x 0.75 | 7.2 |  | H05V2V2-F
[18 empty] | 03050132001z | [30 empty] | 4 G 0.75 | 7.2 |  | H05V2V2-F
[18 empty] | 03050133001z | [30 empty] | 4 x 1.0 | 7.7 |  | H05V2V2-F
[18 empty] | 03050134001z | [30 empty] | 4 G 1.0 | 7.7 |  | H05V2V2-F
[18 empty] | 03050135001z | [30 empty] | 4 x 1.5 | 9.0 |  | H05V2V2-F
[18 empty] | 03050136001z | [30 empty] | 4 G 1.5 | 9.0 |  | H05V2V2-F
[18 empty] | 03050137001z | [30 empty] | 4 x 2.5 | 10.8 |  | H05V2V2-F
[18 empty] | 03050138001z | [30 empty] | 4 G 2.5 | 10.8 |  | H05V2V2-F
[18 empty] | 03050139001z | [30 empty] | 4 x 4 | 12.2 |  | H05V2V2-F
[18 empty] | 03050140001z | [30 empty] | 4 G 4 | 12.2 |  | H05V2V2-F
[18 empty] | 03050141001z | [30 empty] | 5 x 0.75 | 8.0 |  | H05V2V2-F
[18 empty] | 03050142001z | [30 empty] | 5 G 0.75 | 8.0 |  | H05V2V2-F
[18 empty] | 03050143001z | [30 empty] | 5 x 1.0 | 8.3 |  | H05V2V2-F
[18 empty] | 03050144001z | [30 empty] | 5 G 1.0 | 8.3 |  | H05V2V2-F
[18 empty] | 03050145001z | [30 empty] | 5 x 1.5 | 10.0 |  | H05V2V2-F
[18 empty] | 03050146001z | [30 empty] | 5 G 1.5 | 10.0 |  | H05V2V2-F
[18 empty] | 03050147001z | [30 empty] | 5 x 2.5 | 12.0 |  | H05V2V2-F
[18 empty] | 03050148001z | [30 empty] | 5 G 2.5 | 12.0 |  | H05V2V2-F
[18 empty] | 03050149001z | [30 empty] | 5 x 4 | 13.7 |  | H05V2V2-F
[18 empty] | 03050150001z | [30 empty] | 5 G 4 | 13.7 |  | H05V2V2-F
https://www.rrkabel.com/control-cable/control-cable-jb-ycy | JB-YCY | ['https://www.rrkabel.com/Uploads/Products/32/ProductZoomForMoreDetailsImage/JB-YCY.jpg', 'https://www.rrkabel.com/Uploads/Products/32/ProductZoomImage/JB-YCY-1.jpg', 'https://www.rrkabel.com/Uploads/Products/94/ProductFeaturesDetails/outer-sheath-12.png', 'https://www.rrkabel.com/Uploads/Products/94/ProductFeaturesDetails/outer-sheath-12.png'] | ['PVC self-extinguishing and flame retardant according to EN 60332-1-2.'] | [21 empty] | ['For use as a data and control cable in machinery, computer systems etc. as well as a signal cable for electronics. The high level of screening ensures a high degree of interference protection. The dense screening assures disturbance-free transmission of all signals and impulses. The PVC-inner sheaths of these cables raise the mechanical strength. The applied clear transparent PVC outer sheath accentuates the optical view of the tinned copper braid. These cables are suitable for flexible use for medium mechanical stresses with free movements.'] | [5 empty] | ['Adapted to DIN/BS EN 50525-2-51.'] | ['U', 'o', '/ U 300 / 500V up to 1.5 mm². UO / U 450 / 750V for 2.5 mm² and above'] | ['Min. 20 GΩ x cm'] | ['Flexing -5°C to +70°C. Fixed installation -30°C to +70°C', 'Minimum Bending Radius: Flexing 20 x cable ø. Fixed installation 6 x cable ø', 'Test Voltage : 4000V'] | [18 empty] | ['Min. 8000V']
[54 empty] | 30601010216 | 2 x 0.5 | 7.9 | 37 | 124
[54 empty] | 30601020116 | 3G 0.5 | 8.3 | 44 | 139
[54 empty] | 30601030116 | 4G 0.5 | 8.8 | 53 | 168
[54 empty] | 30601040116 | 5G 0.5 | 9.6 | 60 | 205
[54 empty] | 30601050116 | 7G 0.5 | 10.2 | 76 | 243
[54 empty] | 30601060216 | 2 x 0.75 | 8.3 | 44 | 140
[54 empty] | 30601070116 | 3G 0.75 | 8.7 | 54 | 160
[54 empty] | 30601080116 | 4G 0.75 | 9.5 | 66 | 198
[54 empty] | 30601090116 | 5G 0.75 | 10.1 | 78 | 239
[54 empty] | 30601100116 | 7G 0.75 | 10.8 | 99 | 286
[54 empty] | 30601110216 | 2 x 1 | 8.6 | 53 | 156
[54 empty] | 30601120116 | 3G 1 | 9.2 | 65 | 182
[54 empty] | 30601130116 | 4G 1 | 9.8 | 79 | 221
[54 empty] | 30601140116 | 5G 1 | 10.7 | 94 | 272
[54 empty] | 30601150116 | 7G 1 | 11.5 | 122 | 328
[54 empty] | 30601160216 | 2 x 1.5 | 9.7 | 66 | 198
[54 empty] | 30601170116 | 3G 1.5 | 10.2 | 87 | 231
[54 empty] | 30601180116 | 4G 1.5 | 11.1 | 106 | 286
[54 empty] | 30601190116 | 5G 1.5 | 12.4 | 129 | 368
[54 empty] | 30601200116 | 7G 1.5 | 13.2 | 165 | 442
[54 empty] | 30601210216 | 2 x 2.5 | 11.2 | 95 | 271
[54 empty] | 30601220116 | 3G 2.5 | 11.8 | 126 | 318
[54 empty] | 30601230116 | 4G 2.5 | 13.1 | 159 | 412
[54 empty] | 30601240116 | 5G 2.5 | 14.3 | 193 | 511
[54 empty] | 30601250116 | 7G 2.5 | 15.4 | 257 | 624
[54 empty] | 30601260116 | 4G 4 | 13.4 | 264 | 565
[54 empty] | 30601270116 | 5G 4 | 14.8 | 317 | 697
[54 empty] | 30601280116 | 4G 6 | 15.6 | 365 | 732
[54 empty] | 30601290116 | 5G 6 | 17 | 442 | 909
[54 empty] | 30601300116 | 3G 10 | 17.8 | 453 | 889
[54 empty] | 30601310116 | 4G 10 | 19.7 | 580 | 1125
[54 empty] | 30601320116 | 5G 10 | 21.6 | 711 | 1408
[54 empty] | 30601330116 | 3G 16 | 20.7 | 707 | 1274
[54 empty] | 30601340116 | 4G 16 | 22.6 | 917 | 1618
[54 empty] | 30601350116 | 5G 16 | 25.2 | 1128 | 2047
[54 empty] | 30601330116 | 3G 25 | 26.3 | 1064 | 1965
[54 empty] | 30601340116 | 4G 25 | 28.9 | 1386 | 2512
[54 empty] | 30601350116 | 5G 25 | 31.8 | 1708 | 3153
[54 empty] | 30601360116 | 3G 35 | 29.4 | 1453 | 2554
[54 empty] | 30601370116 | 4G 35 | 32.2 | 1900 | 3259
[54 empty] | 30601380116 | 5G 35 | 36 | 2347 | 4133
[54 empty] | 30601390116 | 3G 50 | 35.1 | 2048 | 3653
[54 empty] | 30601380116 | 4G 50 | 38.8 | 2688 | 4701
[54 empty] | 30601390116 | 4G 70 | 43.7 | 3732 | 6229
[54 empty] | 30601400116 | 4G 95 | 50.4 | 4915 | 8123
[54 empty] | 30601410116 | 4G 120 | 56.8 | 6198 | 10118
[54 empty] | 30601420116 | 4G 150 | 62.2 | 7600 | 12511
[54 empty] | 30601430116 | 4G 185 | 67.8 | 9334 | 15306
https://www.rrkabel.com/control-cable/control-cable-jb-ysy | JB-YSY | ['https://www.rrkabel.com/Uploads/Products/33/ProductZoomForMoreDetailsImage/JB-YSY-1.jpg', 'https://www.rrkabel.com/Uploads/Products/33/ProductZoomImage/JB-YSY.jpg', 'https://www.rrkabel.com/Uploads/Products/97/ProductFeaturesDetails/outer-sheath-9.png', 'https://www.rrkabel.com/Uploads/Products/97/ProductFeaturesDetails/outer-sheath-9.png'] | ['Bare copper, fine wire conductors, to EN 60228 Cl. 5. Core insulation of TI2, EN 50363-3.'] | [21 empty] | ['These cables are used as measuring and control cables in food processing industries, packaging industries, tool machinery, plant installation and power stations. The steel braid ensures best possible protection against mechanical damage. The galvanized coating on the steel wire braiding not only helps protect against corrosion, but also notably improves the soldering properties.'] | [5 empty] | ['Adapted to DIN/BS EN 50525-2-51.'] | ['U', 'o', '/ U 300 / 500V up to 1.5 mm². UO/U 450/750V for 2.5 mm² and above'] | ['Min. 20 GΩ x cm'] | ['Flexing -5°C to +70°C; Fixed installation -30°C to +70°C Minimum Bending Radius : Flexing 20 x cable ø. Fixed installation 6 x cable ø Test Voltage : 4000V'] |  |  |  | ['PVC self-extinguishing and flame retardant according to EN 60332-1-2.']
[54 empty] | 03070101021z |  | 9 |  |  | 2 x 0.75 | 18 | 120
[54 empty] | 03070102011z |  | 9.4 |  |  | 3G 0.75 | 27 | 138
[54 empty] | 03070103011z |  | 10.2 |  |  | 4G 0.75 | 36 | 176
[54 empty] | 03070104011z |  | 10.9 |  |  | 5G 0.75 | 44 | 204
[54 empty] | 03070105011z |  | 11.7 |  |  | 7G 0.75 | 62 | 250
[54 empty] | 03070106011z |  | 14.4 |  |  | 12G 0.75 | 107 | 398
[54 empty] | 03070107021z |  | 9.3 |  |  | 2 x 1 | 24 | 129
[54 empty] | 03070108011z |  | 9.9 |  |  | 3G 1 | 36 | 166
[54 empty] | 03070109011z |  | 10.6 |  |  | 4G 1 | 47 | 196
[54 empty] | 03070110011z |  | 11.5 |  |  | 5G 1 | 59 | 234
[54 empty] | 03070111011z |  | 12.3 |  |  | 7G 1 | 83 | 290
[54 empty] | 03070112011z |  | 19.5 |  |  | 25G 1 | 296 | 857
[54 empty] | 03070113021z |  | 10.4 |  |  | 2 x 1.5 | 35 | 171
[54 empty] | 03070114011z |  | 10.9 |  |  | 3G 1.5 | 52 | 205
[54 empty] | 03070115011z |  | 11.9 |  |  | 4G 1.5 | 69 | 252
[54 empty] | 03070116011z |  | 13.1 |  |  | 5G 1.5 | 87 | 307
[54 empty] | 03070117011z |  | 14.1 |  |  | 7G 1.5 | 122 | 381
[54 empty] | 03070118011z |  | 17.3 |  |  | 12G 1.5 | 208 | 618
[54 empty] | 03070119011z |  | 19.7 |  |  | 18G 1.5 | 313 | 873
[54 empty] | 03070120011z |  | 22.6 |  |  | 25G 1.5 | 434 | 1183
[54 empty] | 03070121011z |  | 24.7 |  |  | 32G 1.5 | 556 | 1480
[54 empty] | 03070122021z |  | 11.9 |  |  | 2 x 2.5 | 58 | 238
[54 empty] | 03070123011z |  | 12.5 |  |  | 3G 2.5 | 87 | 285
[54 empty] | 03070124011z |  | 13.8 |  |  | 4G 2.5 | 116 | 371
[54 empty] | 03070125011z |  | 15 |  |  | 5G 2.5 | 145 | 442
[54 empty] | 03070126011z |  | 16.3 |  |  | 7G 2.5 | 203 | 558
[54 empty] | 03070127021z |  | 12.9 |  |  | 2 x 4 | 92 | 304
[54 empty] | 03070128011z |  | 15 |  |  | 4G 4 | 184 | 477
[54 empty] | 03070129011z |  | 16.4 |  |  | 5G 4 | 230 | 574
[54 empty] | 03070130011z |  | 15.2 |  |  | 3G 6 | 207 | 492
[54 empty] | 03070131011z |  | 16.6 |  |  | 4G 6 | 276 | 638
[54 empty] | 03070132011z |  | 18.1 |  |  | 5G 6 | 345 | 770
[54 empty] | 03070133011z |  | 21.3 |  |  | 4G 10 | 470 | 1042
[54 empty] | 03070134011z |  | 23.3 |  |  | 5G 10 | 588 | 1270
[54 empty] | 03070135011z |  | 24.1 |  |  | 4G 16 | 783 | 1479
[54 empty] | 03070136011z |  | 26.6 |  |  | 5G 16 | 979 | 1858
[54 empty] | 03070137011z |  | 29.4 |  |  | 4G 25 | 1218 | 2258
[54 empty] | 03070138011z |  | 32.6 |  |  | 5G 25 | 1522 | 2831
[54 empty] | 03070139011z |  | 32.4 |  |  | 4G 35 | 1715 | 2955
[54 empty] | 03070140011z |  | 36 |  |  | 5G 35 | 2144 | 3711
[54 empty] | 03070141011z |  | 38.8 |  |  | 4G 50 | 2461 | 4256
https://www.rrkabel.com/control-cable/jb-black-kv | JB-BLACK 0.6/1 Kv | ['https://www.rrkabel.com/Uploads/Products/34/ProductZoomForMoreDetailsImage/JB-BK-0.6-1-KV-1.jpg', 'https://www.rrkabel.com/Uploads/Products/34/ProductZoomImage/JB-BK-0.6-1-KV.jpg', 'https://www.rrkabel.com/Uploads/Products/100/ProductFeaturesDetails/sheath-23.png', 'https://www.rrkabel.com/Uploads/Products/100/ProductFeaturesDetails/sheath-23.png'] | ['Bare copper, fine wire conductors, to EN 60228 Cl.5. Core insulation of PVC, TI2 to EN 50363-3.'] | [21 empty] | ['For flexible use with medium and free movement without tensile stress or forced movements in dry, moist and wet rooms as well as outside (fixed installation). These cables are used for manufacturing machines, machine tools. Also used in conveyor belts and product lines.'] | [5 empty] | ['Adapted to DIN VDE 0262, DIN VDE 0281 Part 13 with increased insulation thickness for 1 kV.'] | ['UO / U 0.6 / 1 kV'] | ['Min. 20 GΩ x cm'] | ['Occasional flexing -5°C to +70°C. Fixed installation -30°C to +70°C'] |  | ['4000V'] |  | ['PVC self-extinguishing and flame retardant according to EN 60332-1-2. UV & weather resistant according to ASTM G 154.Ozone resistant according to EN 50396.'] | [12 empty] | ['Flexing 15 x cable ø. Fixed installation 4 x cable ø']
[54 empty] | 30800200001 |  | 8.6 | 19 | 101 | 2 x 1
[54 empty] | 30800310001 |  | 9 | 28 | 117 | 3G 1
[54 empty] | 30800410001 |  | 9.6 | 38 | 138 | 4G 1
[54 empty] | 30800510001 |  | 10.4 | 47 | 164 | 5G 1
[54 empty] | 30800201105 |  | 9.6 | 28 | 129 | 2 x 1.5
[54 empty] | 30800311105 |  | 10.1 | 42 | 152 | 3G 1.5
[54 empty] | 30800411105 |  | 10.8 | 56 | 181 | 4G 1.5
[54 empty] | 30800511105 |  | 11.7 | 69 | 216 | 5G 1.5
[54 empty] | 30800201205 |  | 10.8 | 46 | 173 | 2 x 2.5
[54 empty] | 30800311205 |  | 11.3 | 69 | 205 | 3G 2.5
[54 empty] | 30800411205 |  | 12.2 | 93 | 249 | 4G 2.5
[54 empty] | 30800511205 |  | 13.3 | 116 | 301 | 5G 2.5
[54 empty] | 30800410004 |  | 13.8 | 147 | 344 | 4G 4
[54 empty] | 30800410006 |  | 15.1 | 221 | 450 | 4G 6
[54 empty] | 30800410010 |  | 18.7 | 376 | 723 | 4G 10
[54 empty] | 30800410016 |  | 21.3 | 626 | 1058 | 4G 16
[54 empty] | 30800410025 |  | 26.2 | 974 | 1623 | 4G 25
[54 empty] | 30800410035 |  | 29.1 | 1372 | 2150 | 4G 35
[54 empty] | 30800410050 |  | 35.6 | 1968 | 3144 | 4G 50
[54 empty] | 30800410070 |  | 40.5 | 2747 | 4245 | 4G 70
[54 empty] | 30800410095 |  | 46.6 | 3663 | 5639 | 4G 95
[54 empty] | 30800410120 |  | 53.3 | 4639 | 7242 | 4G 120
https://www.rrkabel.com/control-cable/control-cable-jz-500 | JZ-500 | ['https://www.rrkabel.com/Uploads/Products/35/ProductZoomForMoreDetailsImage/JZ-500.jpg', 'https://www.rrkabel.com/Uploads/Products/35/ProductZoomImage/JZ-500-1.jpg', 'https://www.rrkabel.com/Uploads/Products/103/ProductFeaturesDetails/jz 500.png', 'https://www.rrkabel.com/Uploads/Products/103/ProductFeaturesDetails/jz 500.png'] | [22 empty] | ['These cables are used for flexible use for medium mechanical stresses with free movement without tensile stress of forced movements in dry, moist and wet rooms but not suitable for outdoor installation. Fit for measuring and control cables in tool machines, conveyor belts production lines in machinery production, in air-conditioning and steel production.'] | [5 empty] | ['Requirement adapted to DIN VDE 0245, 0281, 0293, 0295.'] | ['UO / U 300 / 500V'] | ['Min. 20 GΩ x cm'] | ['Flexing -5°C to +70°C. Fixed installation -30°C to +70°C Minimum Bending Radius : Flexing 7.5 x cable ø. Fixed installation 4 x cable ø Test Voltage : 4000V'] |  |  | ['Bare copper, fine wire conductors, to EN 60228 Cl.5. Core insulation of special PVC TI2 EN 50363-3.Black core with continuous white numbering according to DIN VDE 0293. Green/yellow earth core in the outer layer (3 cores and above).Cores stranded in layers with optimal lay-length. Outer sheath of special PVC, TM2 to EN 50363-4.1. Colour grey (RAL 7001).'] | ['PVC self-extinguishing and flame retardant according to EN 60332-1-2.JZ-500 is also available in oil resistant variant as JZ-500 OR. The outer sheath provided here is of special PVC, TM5 to EN 50363 -4.1. For Oil Resistant sheath kindly add "OR" after the part nos.']
[18 empty] | 30900211050 | [30 empty] | 2 x 0.5 | [12 empty] | 4.8 | 9.5 | 35
[18 empty] | 30900311050 | [30 empty] | 3G 0.5 | [12 empty] | 5.1 | 14 | 42
[18 empty] | 30900301050 | [30 empty] | 3 x 0.5 | [12 empty] | 5.1 | 14.2 | 42
[18 empty] | 30900411050 | [30 empty] | 4G 0.5 | [12 empty] | 5.5 | 19 | 49
[18 empty] | 30900401050 | [30 empty] | 4 x 0.5 | [12 empty] | 5.5 | 19 | 49
[18 empty] | 30900511050 | [30 empty] | 5G 0.5 | [12 empty] | 6 | 24 | 61
[18 empty] | 30900501050 | [30 empty] | 5 x 0.5 | [12 empty] | 6 | 24 | 61
[18 empty] | 30900611050 | [30 empty] | 6G 0.5 | [12 empty] | 6.6 | 28.5 | 74
[18 empty] | 30900711050 | [30 empty] | 7G 0.5 | [12 empty] | 6.7 | 33.5 | 76
[18 empty] | 30900701050 | [30 empty] | 7 x 0.5 | [12 empty] | 6.6 | 33.5 | 76
[18 empty] | 30900811050 | [30 empty] | 8G 0.5 | [12 empty] | 7.4 | 38 | 98
[18 empty] | 30900801050 | [30 empty] | 8 x 0.5 | [12 empty] | 7.4 | 38 | 98
[18 empty] | 30901011050 | [30 empty] | 10G 0.5 | [12 empty] | 8.4 | 47.5 | 124
[18 empty] | 30901211050 | [30 empty] | 12G 0.5 | [12 empty] | 8.7 | 57 | 133
[18 empty] | 30901201050 | [30 empty] | 12 x 0.5 | [12 empty] | 8.7 | 57 | 133
[18 empty] | 30901411050 | [30 empty] | 14G 0.5 | [12 empty] | 9.1 | 66.5 | 162
[18 empty] | 30901611050 | [30 empty] | 16G 0.5 | [12 empty] | 9.6 | 76 | 175
[18 empty] | 30901811050 | [30 empty] | 18G 0.5 | [12 empty] | 10.2 | 85.5 | 191
[18 empty] | 30902011050 | [30 empty] | 20G 0.5 | [12 empty] | 10.8 | 95 | 227
[18 empty] | 30902111050 | [30 empty] | 21G 0.5 | [12 empty] | 10.8 | 100 | 234
[18 empty] | 30902511050 | [30 empty] | 25G 0.5 | [12 empty] | 11.2 | 118.5 | 280
[18 empty] | 30903011050 | [30 empty] | 30G 0.5 | [12 empty] | 12.7 | 142.5 | 315
[18 empty] | 30903211050 | [30 empty] | 32G 0.5 | [12 empty] | 13.2 | 152 | 340
[18 empty] | 30903411050 | [30 empty] | 34G 0.5 | [12 empty] | 13.8 | 161.5 | 355
[18 empty] | 30904011050 | [30 empty] | 40G 0.5 | [12 empty] | 14.4 | 190 | 408
[18 empty] | 30904211050 | [30 empty] | 42G 0.5 | [12 empty] | 15 | 199 | 440
[18 empty] | 30905011050 | [30 empty] | 50G 0.5 | [12 empty] | 15.8 | 237 | 552
[18 empty] | 30905211050 | [30 empty] | 52G 0.5 | [12 empty] | 16.3 | 246.5 | 560
[18 empty] | 30906111050 | [30 empty] | 61G 0.5 | [12 empty] | 17.4 | 289.5 | 646
[18 empty] | 30906511050 | [30 empty] | 65G 0.5 | [12 empty] | 17.8 | 308.5 | 687
[18 empty] | 30908011050 | [30 empty] | 80G 0.5 | [12 empty] | 19.4 | 379.5 | 853
[18 empty] | 30910011050 | [30 empty] | 100G 0.5 | [12 empty] | 22.8 | 474 | 1085
[18 empty] | 30900201075 | [30 empty] | 2 x 0.75 | [12 empty] | 5.3 | 14.5 | 44
[18 empty] | 30900311075 | [30 empty] | 3G 0.75 | [12 empty] | 5.6 | 21.5 | 54
[18 empty] | 30900301075 | [30 empty] | 3 x 0.75 | [12 empty] | 5.6 | 21.5 | 54
[18 empty] | 30900411075 | [30 empty] | 4G 0.75 | [12 empty] | 6.2 | 28.5 | 71
[18 empty] | 30900401075 | [30 empty] | 4 x 0.75 | [12 empty] | 6.2 | 28.5 | 71
[18 empty] | 30900511075 | [30 empty] | 5G 0.75 | [12 empty] | 6.8 | 36 | 81
[18 empty] | 30900501075 | [30 empty] | 5 x 0.75 | [12 empty] | 6.8 | 36 | 81
[18 empty] | 30900611075 | [30 empty] | 6G 0.75 | [12 empty] | 7.4 | 43 | 100
[18 empty] | 30900601075 | [30 empty] | 6 x 0.75 | [12 empty] | 7.4 | 43 | 100
[18 empty] | 30900711075 | [30 empty] | 7G 0.75 | [12 empty] | 7.4 | 50 | 103
[18 empty] | 30900701075 | [30 empty] | 7 x 0.75 | [12 empty] | 7.4 | 50 | 103
[18 empty] | 30900811075 | [30 empty] | 8G 0.75 | [12 empty] | 8.3 | 57 | 142
[18 empty] | 30900801075 | [30 empty] | 8 x 0.75 | [12 empty] | 8.3 | 57 | 142
[18 empty] | 30900911075 | [30 empty] | 9G 0.75 | [12 empty] | 9 | 64 | 156
[18 empty] | 30901011075 | [30 empty] | 10G 0.75 | [12 empty] | 9.4 | 71 | 166
[18 empty] | 30901211075 | [30 empty] | 12G 0.75 | [12 empty] | 9.8 | 85.5 | 180
[18 empty] | 30901201075 | [30 empty] | 12 x 0.75 | [12 empty] | 9.8 | 85.5 | 180
[18 empty] | 30901411075 | [30 empty] | 14G 0.75 | [12 empty] | 10.3 | 100 | 205
[18 empty] | 30901511075 | [30 empty] | 15G 0.75 | [12 empty] | 10.9 | 107 | 230
[18 empty] | 30901811075 | [30 empty] | 18G 0.75 | [12 empty] | 11.5 | 128 | 260
[18 empty] | 30901911075 | [30 empty] | 19G 0.75 | [12 empty] | 11.5 | 135 | 270
[18 empty] | 30902011075 | [30 empty] | 20G 0.75 | [12 empty] | 12.2 | 142.5 | 300
[18 empty] | 30902111075 | [30 empty] | 21G 0.75 | [12 empty] | 12.2 | 149.5 | 311
[18 empty] | 30902511075 | [30 empty] | 25G 0.75 | [12 empty] | 12.6 | 178 | 376
[18 empty] | 30902711075 | [30 empty] | 27G 0.75 | [12 empty] | 13.9 | 192 | 405
[18 empty] | 30903211075 | [30 empty] | 32G 0.75 | [12 empty] | 15 | 228 | 455
[18 empty] | 30903411075 | [30 empty] | 34G 0.75 | [12 empty] | 15.6 | 242 | 470
[18 empty] | 30903711075 | [30 empty] | 37G 0.75 | [12 empty] | 15.6 | 263 | 515
[18 empty] | 30904011075 | [30 empty] | 40G 0.75 | [12 empty] | 16.3 | 284.5 | 532
[18 empty] | 30904111075 | [30 empty] | 41G 0.75 | [12 empty] | 17 | 292 | 570
[18 empty] | 30904211075 | [30 empty] | 42G 0.75 | [12 empty] | 17 | 299 | 600
[18 empty] | 30905011075 | [30 empty] | 50G 0.75 | [12 empty] | 18 | 356 | 690
[18 empty] | 30906111075 | [30 empty] | 61G 0.75 | [12 empty] | 19.7 | 434 | 835
[18 empty] | 30906511075 | [30 empty] | 65G 0.75 | [12 empty] | 20.3 | 462.5 | 890
[18 empty] | 30908011075 | [30 empty] | 80G 0.75 | [12 empty] | 22.9 | 569 | 1087
[18 empty] | 30910011075 | [30 empty] | 100G 0.75 | [12 empty] | 26 | 711.5 | 1410
[18 empty] | 30900200001 | [30 empty] | 2 x 1 | [12 empty] | 5.6 | 19 | 52
[18 empty] | 30900310001 | [30 empty] | 3G 1 | [12 empty] | 6 | 28.5 | 66
[18 empty] | 30900300001 | [30 empty] | 3 x 1 | [12 empty] | 6 | 28.5 | 66
[18 empty] | 30900410001 | [30 empty] | 4G 1 | [12 empty] | 6.6 | 38 | 82
[18 empty] | 30900400001 | [30 empty] | 4 x 1 | [12 empty] | 6.6 | 38 | 82
[18 empty] | 30900510001 | [30 empty] | 5G 1 | [12 empty] | 7.2 | 47.5 | 100
[18 empty] | 30900500001 | [30 empty] | 5 x 1 | [12 empty] | 7.2 | 47.5 | 100
[18 empty] | 30900610001 | [30 empty] | 6G 1 | [12 empty] | 7.9 | 57 | 122
[18 empty] | 30900710001 | [30 empty] | 7G 1 | [12 empty] | 7.9 | 66.5 | 142
[18 empty] | 30900700001 | [30 empty] | 7 x 1 | [12 empty] | 7.9 | 66.5 | 142
[18 empty] | 30900810001 | [30 empty] | 8G 1 | [12 empty] | 8.9 | 76 | 165
[18 empty] | 30900910001 | [30 empty] | 9G 1 | [12 empty] | 9.6 | 85.5 | 190
[18 empty] | 30901010001 | [30 empty] | 10G 1 | [12 empty] | 10.1 | 95 | 205
[18 empty] | 30901000001 | [30 empty] | 10 x 1 | [12 empty] | 10.1 | 95 | 205
[18 empty] | 30901210001 | [30 empty] | 12G 1 | [12 empty] | 10.4 | 114 | 230
[18 empty] | 30901200001 | [30 empty] | 12 x 1 | [12 empty] | 10.4 | 114 | 230
[18 empty] | 30901410001 | [30 empty] | 14G 1 | [12 empty] | 11 | 133 | 258
[18 empty] | 30901610001 | [30 empty] | 16G 1 | [12 empty] | 11.6 | 152 | 293
[18 empty] | 30901810001 | [30 empty] | 18G 1 | [12 empty] | 12.3 | 171 | 330
[18 empty] | 30901800001 | [30 empty] | 18 x 1 | [12 empty] | 12.3 | 171 | 330
[18 empty] | 30901910001 | [30 empty] | 19G 1 | [12 empty] | 12.3 | 180.5 | 337
[18 empty] | 30902010001 | [30 empty] | 20G 1 | [12 empty] | 13 | 190 | 370
[18 empty] | 30902000001 | [30 empty] | 20 x 1 | [12 empty] | 13 | 190 | 370
[18 empty] | 30902110001 | [30 empty] | 21G 1 | [12 empty] | 13 | 199.5 | 383
[18 empty] | 30902410001 | [30 empty] | 24G 1 | [12 empty] | 13.5 | 228 | 420
[18 empty] | 30902510001 | [30 empty] | 25G 1 | [12 empty] | 13.5 | 237.5 | 435
[18 empty] | 30902500001 | [30 empty] | 25 x 1 | [12 empty] | 13.5 | 237.5 | 435
[18 empty] | 30902610001 | [30 empty] | 26G 1 | [12 empty] | 13.5 | 246.5 | 445
[18 empty] | 30902710001 | [30 empty] | 27G 1 | [12 empty] | 14.8 | 256 | 502
[18 empty] | 30903010001 | [30 empty] | 30G 1 | [12 empty] | 15.4 | 284.5 | 535
[18 empty] | 30903410001 | [30 empty] | 34G 1 | [12 empty] | 16.7 | 322.5 | 620
[18 empty] | 30903610001 | [30 empty] | 36G 1 | [12 empty] | 16.7 | 341.5 | 635
[18 empty] | 30903710001 | [30 empty] | 37G 1 | [12 empty] | 16.7 | 351 | 680
[18 empty] | 30904010001 | [30 empty] | 40G 1 | [12 empty] | 17.5 | 379.5 | 730
[18 empty] | 30904000001 | [30 empty] | 40 x 1 | [12 empty] | 17.5 | 379.5 | 730
[18 empty] | 30904110001 | [30 empty] | 41G 1 | [12 empty] | 18.2 | 389 | 740
[18 empty] | 30904210001 | [30 empty] | 42G 1 | [12 empty] | 18.2 | 398.5 | 749
[18 empty] | 30905010001 | [30 empty] | 50G 1 | [12 empty] | 19.3 | 474.5 | 870
[18 empty] | 30905610001 | [30 empty] | 56G 1 | [12 empty] | 20.5 | 531 | 972
[18 empty] | 30906110001 | [30 empty] | 61G 1 | [12 empty] | 21.2 | 578.5 | 1050
[18 empty] | 30906510001 | [30 empty] | 65G 1 | [12 empty] | 21.8 | 616.5 | 1112
[18 empty] | 30908010001 | [30 empty] | 80G 1 | [12 empty] | 24.3 | 759 | 1380
[18 empty] | 30910010001 | [30 empty] | 100G 1 | [12 empty] | 27.8 | 948.5 | 1767
[18 empty] | 30900201105 | [30 empty] | 2 x 1.5 | [12 empty] | 6.3 | 29 | 69
[18 empty] | 30900311105 | [30 empty] | 3G 1.5 | [12 empty] | 6.7 | 43.5 | 87
[18 empty] | 30900301105 | [30 empty] | 3 x 1.5 | [12 empty] | 6.7 | 43.5 | 87
[18 empty] | 30900411105 | [30 empty] | 4G 1.5 | [12 empty] | 7.3 | 58 | 107
[18 empty] | 30900401105 | [30 empty] | 4 x 1.5 | [12 empty] | 7.3 | 58 | 107
[18 empty] | 30900511105 | [30 empty] | 5G 1.5 | [12 empty] | 8 | 72.5 | 135
[18 empty] | 30900501105 | [30 empty] | 5 x 1.5 | [12 empty] | 8 | 72.5 | 135
[18 empty] | 30900611105 | [30 empty] | 6G 1.5 | [12 empty] | 8.8 | 86.7 | 162
[18 empty] | 30900711105 | [30 empty] | 7G 1.5 | [12 empty] | 8.8 | 101 | 168
[18 empty] | 30900701105 | [30 empty] | 7 x 1.5 | [12 empty] | 8.8 | 101 | 168
[18 empty] | 30900811105 | [30 empty] | 8G 1.5 | [12 empty] | 9.9 | 116 | 213
[18 empty] | 30900801105 | [30 empty] | 8 x 1.5 | [12 empty] | 9.9 | 116 | 213
[18 empty] | 30900911105 | [30 empty] | 9G 1.5 | [12 empty] | 10.8 | 130 | 248
[18 empty] | 30901011105 | [30 empty] | 10G 1.5 | [12 empty] | 11.3 | 145 | 263
[18 empty] | 30901111105 | [30 empty] | 11G 1.5 | [12 empty] | 11.3 | 159 | 299
[18 empty] | 30901211105 | [30 empty] | 12G 1.5 | [12 empty] | 11.7 | 173.5 | 295
[18 empty] | 30901201105 | [30 empty] | 12 x 1.5 | [12 empty] | 11.7 | 173.5 | 295
[18 empty] | 30901411105 | [30 empty] | 14G 1.5 | [12 empty] | 12.4 | 202.5 | 340
[18 empty] | 30901611105 | [30 empty] | 16G 1.5 | [12 empty] | 13.1 | 202.5 | 382
[18 empty] | 30901811105 | [30 empty] | 18G 1.5 | [12 empty] | 13.9 | 260 | 433
[18 empty] | 30902111105 | [30 empty] | 21G 1.5 | [12 empty] | 14.8 | 303.5 | 505
[18 empty] | 30902511105 | [30 empty] | 25G 1.5 | [12 empty] | 15.3 | 361 | 605
[18 empty] | 30902611105 | [30 empty] | 26G 1.5 | [12 empty] | 15.3 | 361 | 622
[18 empty] | 30903211105 | [30 empty] | 32G 1.5 | [12 empty] | 18.2 | 462.5 | 799
[18 empty] | 30903411105 | [30 empty] | 34G 1.5 | [12 empty] | 18.9 | 491 | 812
[18 empty] | 30904111105 | [30 empty] | 41G 1.5 | [12 empty] | 20 | 592.5 | 960
[18 empty] | 30905011105 | [30 empty] | 50G 1.5 | [12 empty] | 21.9 | 722.5 | 1240
[18 empty] | 30906111105 | [30 empty] | 61G 1.5 | [12 empty] | 24 | 881.5 | 1420
[18 empty] | 30906511105 | [30 empty] | 65G 1.5 | [12 empty] | 24.7 | 939 | 1570
[18 empty] | 30900201205 | [30 empty] | 2 x 2.5 | [12 empty] | 7.5 | 40.1 | 101
[18 empty] | 30900311205 | [30 empty] | 3G 2.5 | [12 empty] | 8 | 61 | 130
[18 empty] | 30900411205 | [30 empty] | 4G 2.5 | [12 empty] | 8.9 | 82 | 162
[18 empty] | 30900511205 | [30 empty] | 5G 2.5 | [12 empty] | 9.8 | 102 | 200
[18 empty] | 30900711205 | [30 empty] | 7G 2.5 | [12 empty] | 10.7 | 142 | 260
[18 empty] | 30901211205 | [30 empty] | 12G 2.5 | [12 empty] | 14.4 | 248 | 452
[18 empty] | 30901411205 | [30 empty] | 14G 2.5 | [12 empty] | 15.2 | 290 | 517
[18 empty] | 30901811205 | [30 empty] | 18G 2.5 | [12 empty] | 17 | 378 | 665
[18 empty] | 30902511205 | [30 empty] | 25G 2.5 | [12 empty] | 18.8 | 525 | 870
[18 empty] | 30903411205 | [30 empty] | 34G 2.5 | [12 empty] | 23.4 | 175 | 1250
[18 empty] | 30905011205 | [30 empty] | 50G 2.5 | [12 empty] | 27 | 1050 | 1810
[18 empty] | 30900310004 | [30 empty] | 3G 4 | [12 empty] | 9.2 | 96 | 185
[18 empty] | 30900410004 | [30 empty] | 4G 4 | [12 empty] | 10.1 | 128 | 230
[18 empty] | 30900510004 | [30 empty] | 5G 4 | [12 empty] | 11.2 | 159.5 | 286
[18 empty] | 30900710004 | [30 empty] | 7G 4 | [12 empty] | 12.3 | 223.5 | 370
[18 empty] | 30901110004 | [30 empty] | 10G 4 | [12 empty] | 16 | 325 | 608
[18 empty] | 30901210004 | [30 empty] | 12G 4 | [12 empty] | 16.6 | 383 | 660
[18 empty] | 30900310006 | [30 empty] | 3G 6 | [12 empty] | 11 | 144 | 277
[18 empty] | 30900410006 | [30 empty] | 4G 6 | [12 empty] | 12.2 | 191.5 | 354
[18 empty] | 30900510006 | [30 empty] | 5G 6 | [12 empty] | 13.5 | 239.5 | 441
[18 empty] | 30900710006 | [30 empty] | 7G 6 | [12 empty] | 14.8 | 335 | 574
[18 empty] | 30900310010 | [30 empty] | 3G 10 | [12 empty] | 13.1 | 244.5 | 436
[18 empty] | 30900410010 | [30 empty] | 4G 10 | [12 empty] | 14.5 | 326 | 548
[18 empty] | 30900510010 | [30 empty] | 5G 10 | [12 empty] | 16 | 407.5 | 676
[18 empty] | 30900710010 | [30 empty] | 7G 10 | [12 empty] | 17.7 | 570.5 | 892
[18 empty] | 30900410016 | [30 empty] | 4G 16 | [12 empty] | 17.8 | 543 | 860
[18 empty] | 30900510016 | [30 empty] | 5G 16 | [12 empty] | 19.7 | 678.5 | 1074
[18 empty] | 30900710016 | [30 empty] | 7G 16 | [12 empty] | 21.8 | 950 | 1392
[18 empty] | 30900410025 | [30 empty] | 4G 25 | [12 empty] | 21.9 | 844.5 | 1335
[18 empty] | 30900510025 | [30 empty] | 5G 25 | [12 empty] | 25.8 | 1055.5 | 1710
[18 empty] | 30900710025 | [30 empty] | 7G 25 | [12 empty] | 28.7 | 1478 | 2184
[18 empty] | 30900410035 | [30 empty] | 4G 35 | [12 empty] | 26.4 | 1189 | 1795
[18 empty] | 30900510035 | [30 empty] | 5G 35 | [12 empty] | 29.6 | 1486.5 | 2251
https://www.rrkabel.com/control-cable/control-cable-jz-ycy | JZ-YCY | ['https://www.rrkabel.com/Uploads/Products/36/ProductZoomForMoreDetailsImage/02.jpg', 'https://www.rrkabel.com/Uploads/Products/36/ProductZoomImage/03.jpg', 'https://www.rrkabel.com/Uploads/Products/106/ProductFeaturesDetails/9-9-9.png', 'https://www.rrkabel.com/Uploads/Products/106/ProductFeaturesDetails/9-9-9.png'] | ['The clear transparent PVC outer sheath accentuates the optical view of the tinned copper braid. PVC self-extinguishing and flame retardant according to EN 60332-1-2.', 'JZ-YCY grey (RAL 7001) is available in oil resistant variant as JZ-YCY OR. The outer sheath provided here is of special PVC TM5 to BS EN 50363 -4.1.', "For oil resistant sheath kindly add 'OR' after the part nos."] | [21 empty] | ['For use as a data and control cable in machinery, computer systems etc. as well as a signal cable for electronics. The high level of screening ensures a high degree of interference protection. The screening density assures disturbance-free transmission of all signals and impulses.', 'Standard', 'Requirements adapted to DIN VDE 0245, 0281 Part 13.'] | [6 empty] | ['U', '0', '/U 300 / 500V'] | ['Min. 20 GΩ x cm'] | ['Flexing -5°C to +70°C. Fixed installation -30°C to +70°C Minimum Bending Radius : Flexing 10 x cable ø. Fixed installation 5 x cable ø Test Voltage : 4000V'] |  |  | ['Bare copper, fine wire conductors, to EN 60228 Cl.5. Core insulation of PVC TI2 EN 50363-3.Black Core with continuous white numbering to DIN VDE 0293. Green/Yellow earth core in outer layer (3 cores and above).Cores stranded in layers with optimal lay-length. Special PVC inner jacket.Tinned copper, braided screen, approx 85% coverage. Transparent special PVC outer sheath.']
[18 empty] | 31000201050 | [30 empty] | 2 x 0.5 | 7.1 | [12 empty] | 21.6 | 76
[18 empty] | 31000311050 | [30 empty] | 3G 0.5 | 7.5 | [12 empty] | 27.6 | 85
[18 empty] | 31000301050 | [30 empty] | 3 X 0.5 | 7.5 | [12 empty] | 27.6 | 85
[18 empty] | 31000411050 | [30 empty] | 4G 0.5 | 8 | [12 empty] | 32.5 | 99
[18 empty] | 31000401050 | [30 empty] | 4 X 0.5 | 8 | [12 empty] | 32.5 | 99
[18 empty] | 31000511050 | [30 empty] | 5G 0.5 | 8.5 | [12 empty] | 38.7 | 114
[18 empty] | 31000501050 | [30 empty] | 5 X 0.5 | 8.5 | [12 empty] | 38.7 | 114
[18 empty] | 31000711050 | [30 empty] | 7G 0.5 | 9.1 | [12 empty] | 47.7 | 136
[18 empty] | 31000701050 | [30 empty] | 7 X 0.5 | 9.1 | [12 empty] | 47.7 | 136
[18 empty] | 31001211050 | [30 empty] | 12G 0.5 | 11.3 | [12 empty] | 75.2 | 198
[18 empty] | 31001201050 | [30 empty] | 12 X 0.5 | 11.3 | [12 empty] | 75.2 | 198
[18 empty] | 31001811050 | [30 empty] | 18G 0.5 | 13 | [12 empty] | 102.2 | 260
[18 empty] | 31002511050 | [30 empty] | 25G 0.5 | 14 | [12 empty] | 153.7 | 353
[18 empty] | 31003011050 | [30 empty] | 30G 0.5 | 15.9 | [12 empty] | 178.7 | 402
[18 empty] | 31004011050 | [30 empty] | 40G 0.5 | 17.6 | [12 empty] | 228 | 515
[18 empty] | 31000201075 | [30 empty] | 2 x 0.75 | 7.7 | [12 empty] | 27.5 | 91
[18 empty] | 31000311075 | [30 empty] | 3G 0.75 | 8.1 | [12 empty] | 36.2 | 103
[18 empty] | 31000301075 | [30 empty] | 3 X 0.75 | 8.1 | [12 empty] | 36.2 | 103
[18 empty] | 31000411075 | [30 empty] | 4G 0.75 | 8.6 | [12 empty] | 42.4 | 122
[18 empty] | 31000401075 | [30 empty] | 4 X 0.75 | 8.6 | [12 empty] | 42.4 | 122
[18 empty] | 31000511075 | [30 empty] | 5G 0.75 | 9.3 | [12 empty] | 48.7 | 142
[18 empty] | 31000501075 | [30 empty] | 5 X 0.75 | 9.3 | [12 empty] | 48.7 | 142
[18 empty] | 31000711075 | [30 empty] | 7G 0.75 | 9.9 | [12 empty] | 64 | 170
[18 empty] | 31000701075 | [30 empty] | 7 X 0.75 | 9.9 | [12 empty] | 64 | 170
[18 empty] | 31001211075 | [30 empty] | 12G 0.75 | 12.5 | [12 empty] | 101.1 | 275
[18 empty] | 31001201075 | [30 empty] | 12 X 0.75 | 12.5 | [12 empty] | 101.1 | 275
[18 empty] | 31001811075 | [30 empty] | 18G 0.75 | 14.6 | [12 empty] | 160.6 | 352
[18 empty] | 31001801075 | [30 empty] | 18 X 0.0.75 | 14.6 | [12 empty] | 160.6 | 352
[18 empty] | 31002511075 | [30 empty] | 25G 0.75 | 15.8 | [12 empty] | 214.1 | 448
[18 empty] | 31003411075 | [30 empty] | 34G 0.75 | 19 | [12 empty] | 279 | 627
[18 empty] | 31004001075 | [30 empty] | 40 X 0.75 | 19.8 | [12 empty] | 337.4 | 691
[18 empty] | 31004111075 | [30 empty] | 41G 0.75 | 20.7 | [12 empty] | 345.2 | 703
[18 empty] | 31000200001 | [30 empty] | 2 x 1 | 8.1 | [12 empty] | 32 | 101
[18 empty] | 31000310001 | [30 empty] | 3G 1 | 8.4 | [12 empty] | 42.2 | 117
[18 empty] | 31000300001 | [30 empty] | 3 x 1 | 8.4 | [12 empty] | 42.2 | 117
[18 empty] | 31000410001 | [30 empty] | 4G 1 | 9.1 | [12 empty] | 50.7 | 139
[18 empty] | 31000400001 | [30 empty] | 4 x 1 | 9.1 | [12 empty] | 50.7 | 139
[18 empty] | 31000510001 | [30 empty] | 5G 1 | 9.7 | [12 empty] | 61.3 | 163
[18 empty] | 31000710001 | [30 empty] | 7G 1 | 10.4 | [12 empty] | 79.5 | 197
[18 empty] | 31001210001 | [30 empty] | 12G 1 | 13.2 | [12 empty] | 146.2 | 300
[18 empty] | 31001610001 | [30 empty] | 16G 1 | 14.7 | [12 empty] | 185.5 | 375
[18 empty] | 31001810001 | [30 empty] | 18G 1 | 15.4 | [12 empty] | 202.5 | 402
[18 empty] | 31002510001 | [30 empty] | 25G 1 | 16.7 | [12 empty] | 271.5 | 525
[18 empty] | 31003410001 | [30 empty] | 34G 1 | 20.2 | [12 empty] | 354 | 700
[18 empty] | 31004110001 | [30 empty] | 41G 1 | 22 | [12 empty] | 437.1 | 880
[18 empty] | 31005010001 | [30 empty] | 50G 1 | 23.1 | [12 empty] | 521.9 | 990
[18 empty] | 31000201105 | [30 empty] | 2 x 1.5 | 8.7 | [12 empty] | 42.1 | 119
[18 empty] | 31000311105 | [30 empty] | 3G 1.5 | 9.2 | [12 empty] | 56 | 140
[18 empty] | 31000301105 | [30 empty] | 3 x 1.5 | 9.2 | [12 empty] | 56 | 140
[18 empty] | 31000411105 | [30 empty] | 4G 1.5 | 9.9 | [12 empty] | 69.1 | 167
[18 empty] | 31000401105 | [30 empty] | 4 x 1.5 | 9.9 | [12 empty] | 69.1 | 167
[18 empty] | 31000511105 | [30 empty] | 5G 1.5 | 10.7 | [12 empty] | 99.2 | 208
[18 empty] | 31000501105 | [30 empty] | 5 x 1.5 | 10.7 | [12 empty] | 99.2 | 208
[18 empty] | 31000711105 | [30 empty] | 7G 1.5 | 11.5 | [12 empty] | 124.6 | 256
[18 empty] | 31000701105 | [30 empty] | 7 x 1.5 | 11.5 | [12 empty] | 124.6 | 256
[18 empty] | 31001211105 | [30 empty] | 12G 1.5 | 14.8 | [12 empty] | 198.6 | 397
[18 empty] | 31001811105 | [30 empty] | 18G 1.5 | 17.1 | [12 empty] | 279.6 | 521
[18 empty] | 31002511105 | [30 empty] | 25G 1.5 | 18.6 | [12 empty] | 375.2 | 709
[18 empty] | 31003411105 | [30 empty] | 34G 1.5 | 22.8 | [12 empty] | 497.4 | 977
[18 empty] | 31004111105 | [30 empty] | 41G 1.5 | 24.6 | [12 empty] | 611.9 | 1168
[18 empty] | 31005011105 | [30 empty] | 50G 1.5 | 25.9 | [12 empty] | 730.1 | 1402
[18 empty] | 31000201205 | [30 empty] | 2 x 2.5 | 10.1 | [12 empty] | 61.2 | 166
[18 empty] | 31000311205 | [30 empty] | 3G 2.5 | 10.7 | [12 empty] | 99.1 | 208
[18 empty] | 31000411205 | [30 empty] | 4G 2.5 | 11.5 | [12 empty] | 121.1 | 253
[18 empty] | 31000511205 | [30 empty] | 5G 2.5 | 12.5 | [12 empty] | 146.4 | 274
[18 empty] | 31000711205 | [30 empty] | 7G 1.5 | 13.5 | [12 empty] | 192.3 | 350
[18 empty] | 31001211205 | [30 empty] | 12G 2.5 | 17.7 | [12 empty] | 304.4 | 585
[18 empty] | 31000200004 | [30 empty] | 2 x 4 | 11.2 | [12 empty] | 104.4 | 211
[18 empty] | 31000410004 | [30 empty] | 4G 4 | 12.9 | [12 empty] | 173.2 | 316
[18 empty] | 31000510004 | [30 empty] | 5G 4 | 14.2 | [12 empty] | 212.4 | 385
[18 empty] | 31000200006 | [30 empty] | 2 x 6 | 13.1 | [12 empty] | 141.6 | 296
[18 empty] | 31000410006 | [30 empty] | 4G 6 | 15.3 | [12 empty] | 250.2 | 450
[18 empty] | 31000510006 | [30 empty] | 5G 6 | 16.7 | [12 empty] | 303.7 | 544
[18 empty] | 31000200010 | [30 empty] | 2 x 10 | 15.3 | [12 empty] | 220.4 | 445
[18 empty] | 31000310010 | [30 empty] | 3G 10 | 16.3 | [12 empty] | 308.7 | 550
[18 empty] | 31000410010 | [30 empty] | 4G 10 | 17.8 | [12 empty] | 395.2 | 680
[18 empty] | 31000510010 | [30 empty] | 5G 10 | 19.5 | [12 empty] | 482.7 | 840
[18 empty] | 31000710010 | [30 empty] | 7G 10 | 21.4 | [12 empty] | 653.4 | 1068
[18 empty] | 31000200016 | [30 empty] | 2 x 16 | 18.3 | [12 empty] | 367.3 | 655
[18 empty] | 31000410016 | [30 empty] | 4G 16 | 21.5 | [12 empty] | 657.4 | 1021
[18 empty] | 31000510016 | [30 empty] | 5G 16 | 23.6 | [12 empty] | 807.2 | 1362
[18 empty] | 31000410025 | [30 empty] | 4G 25 | 26 | [12 empty] | 984.1 | 1618
[18 empty] | 31000510025 | [30 empty] | 5G 25 | 31.6 | [12 empty] | 1210.5 | 1980
[18 empty] | 31000410035 | [30 empty] | 4G 35 | 32 | [12 empty] | 1352 | 2235
[18 empty] | 31000510035 | [30 empty] | 5G 35 | 35.5 | [12 empty] | 1670.1 | 2760
https://www.rrkabel.com/control-cable/control-cable-jz-ysy | JZ-YSY | ['https://www.rrkabel.com/Uploads/Products/37/ProductZoomForMoreDetailsImage/02.jpg', 'https://www.rrkabel.com/Uploads/Products/37/ProductZoomImage/03.jpg', 'https://www.rrkabel.com/Uploads/Products/109/ProductFeaturesDetails/10-10-10.png', 'https://www.rrkabel.com/Uploads/Products/109/ProductFeaturesDetails/10-10-10.png'] | [22 empty] | ['These cables are used as measuring and control cables in tool machinery, plant installation, power stations and in data equipment. The braided screen offers best possible protection against mechanical damage. The galvanised coating on the steel wire braiding not only helps protect against corrosion, but also notably improves the soldering performance.'] | ['Cable Construction', 'Bare copper, fine wire conductors, to EN 60228 Cl.5. Core insulation of PVC TI2, EN 50363-3.Black Core with continuous white numbering to DIN VDE 0293. Green/Yellow earth core in outer layer (3 cores and above).Cores stranded in layers with optimal lay-length. Special PVC inner jacket.Galvanized steel wire screening.Special PVC outer jacket.Colour transparent (also available in grey).'] |  |  |  |  | ['Adapted to DIN VDE 0245, 0281, 0293, 0295.'] | ['U', '0', '/ U 300 / 500V'] | ['Min. 20 GΩ x cm'] | ['Flexing -5°C to +70°C. Fixed installation -30°C to +70°C'] |  | ['4000V'] |  | ['The clear transparent PVC outer sheath accentuates the optical view of the galvanized steel wire braid. PVC self-extinguishing and flame retardant according to EN 60332-1-2JZ-YSY Grey(RAL 7001) is also available in oil resistant variant as JZ-YSY OR. The outer sheath provided here is of special PVC TM5 to BS EN 50363 -4.1.'] | [12 empty] | ['Flexing 20 x cable ø. Fixed installation 6 x cable ø']
[18 empty] | 03110101021z | [30 empty] | 2 x 0.5 | 8 | [12 empty] | 9.5 | 99
[18 empty] | 03110102011z | [30 empty] | 3G 0.5 | 8.3 | [12 empty] | 14 | 109
[18 empty] | 03110103011z | [30 empty] | 4G 0.5 | 8.8 | [12 empty] | 19 | 123
[18 empty] | 03110104011z | [30 empty] | 5G 0.5 | 9.3 | [12 empty] | 24 | 153
[18 empty] | 03110105011z | [30 empty] | 7G 0.5 | 9.9 | [12 empty] | 33.5 | 171
[18 empty] | 03110106011z | [30 empty] | 10G 0.5 | 11.8 | [12 empty] | 47.5 | 246
[18 empty] | 03110107011z | [30 empty] | 12G 0.5 | 12.1 | [12 empty] | 57 | 263
[18 empty] | 03110108011z | [30 empty] | 14G 0.5 | 12.6 | [12 empty] | 66.5 | 289
[18 empty] | 03110109011z | [30 empty] | 18G 0.5 | 13.8 | [12 empty] | 85.5 | 313
[18 empty] | 03110110011z | [30 empty] | 21G 0.5 | 14.4 | [12 empty] | 100 | 354
[18 empty] | 03110111011z | [30 empty] | 25G 0.5 | 14.8 | [12 empty] | 118.5 | 391
[18 empty] | 03110112011z | [30 empty] | 30G 0.5 | 16.5 | [12 empty] | 142.5 | 462
[18 empty] | 03110113011z | [30 empty] | 40G 0.5 | 18.3 | [12 empty] | 190 | 582
[18 empty] | 03110114011z | [30 empty] | 61G 0.5 | 21.5 | [12 empty] | 289.5 | 833
[18 empty] | 03110115021z | [30 empty] | 2 x 0.75 | 8.5 | [12 empty] | 14.5 | 109
[18 empty] | 03110116011z | [30 empty] | 3G 0.75 | 8.9 | [12 empty] | 21.5 | 123
[18 empty] | 03110117011z | [30 empty] | 4G 0.75 | 9.5 | [12 empty] | 28.5 | 157
[18 empty] | 03110118011z | [30 empty] | 5G 0.75 | 10.1 | [12 empty] | 36 | 174
[18 empty] | 03110119011z | [30 empty] | 7G 0.75 | 10.8 | [12 empty] | 50 | 199
[18 empty] | 03110120011z | [30 empty] | 9G 0.75 | 12.5 | [12 empty] | 64 | 261
[18 empty] | 03110121011z | [30 empty] | 12G 0.75 | 13.3 | [12 empty] | 85.5 | 315
[18 empty] | 03110122011z | [30 empty] | 15G 0.75 | 14.5 | [12 empty] | 107 | 363
[18 empty] | 03110123011z | [30 empty] | 18G 0.75 | 15.2 | [12 empty] | 128 | 435
[18 empty] | 03110124011z | [30 empty] | 25G 0.75 | 16.4 | [12 empty] | 178 | 507
[18 empty] | 03110125011z | [30 empty] | 34G 0.75 | 19.7 | [12 empty] | 242 | 730
[18 empty] | 03110126011z | [30 empty] | 50G 0.75 | 22.2 | [12 empty] | 356 | 901
[18 empty] | 03110127021z | [30 empty] | 2 x 1 | 8.9 | [12 empty] | 19 | 120
[18 empty] | 03110128011z | [30 empty] | 3G 1 | 9.3 | [12 empty] | 28.5 | 149
[18 empty] | 03110129011z | [30 empty] | 4G 1 | 9.9 | [12 empty] | 38 | 172
[18 empty] | 03110130011z | [30 empty] | 5G 1 | 10.6 | [12 empty] | 47.5 | 193
[18 empty] | 03110131011z | [30 empty] | 7G 1 | 11.3 | [12 empty] | 66.5 | 232
[18 empty] | 03110132011z | [30 empty] | 8G 1 | 12.3 | [12 empty] | 76 | 260
[18 empty] | 03110133011z | [30 empty] | 9G 1 | 13.2 | [12 empty] | 85.5 | 300
[18 empty] | 03110134011z | [30 empty] | 12G 1 | 14 | [12 empty] | 114 | 373
[18 empty] | 03110135011z | [30 empty] | 14G 1 | 14.6 | [12 empty] | 133 | 406
[18 empty] | 03110136011z | [30 empty] | 18G 1 | 16.1 | [12 empty] | 171 | 504
[18 empty] | 03110137011z | [30 empty] | 20G 1 | 16.8 | [12 empty] | 190 | 522
[18 empty] | 03110138011z | [30 empty] | 25G 1 | 17.4 | [12 empty] | 237.5 | 598
[18 empty] | 03110139011z | [30 empty] | 34G 1 | 20.8 | [12 empty] | 322.5 | 762
[18 empty] | 03110140011z | [30 empty] | 41G 1 | 22.5 | [12 empty] | 389 | 1013
[18 empty] | 03110141011z | [30 empty] | 50G 1 | 23.6 | [12 empty] | 474.5 | 1105
[18 empty] | 03110142011z | [30 empty] | 65G 1 | 26.3 | [12 empty] | 616.5 | 1426
[18 empty] | 03110143021z | [30 empty] | 2 x 1.5 | 9.6 | [12 empty] | 29 | 159
[18 empty] | 03110144011z | [30 empty] | 3G 1.5 | 10 | [12 empty] | 43.5 | 181
[18 empty] | 03110145011z | [30 empty] | 4G 1.5 | 10.7 | [12 empty] | 58 | 206
[18 empty] | 03110146011z | [30 empty] | 5G 1.5 | 11.5 | [12 empty] | 72.5 | 243
[18 empty] | 03110147011z | [30 empty] | 7G 1.5 | 12.3 | [12 empty] | 101 | 302
[18 empty] | 03110148011z | [30 empty] | 8G 1.5 | 13.5 | [12 empty] | 116 | 334
[18 empty] | 03110149011z | [30 empty] | 12G 1.5 | 15.5 | [12 empty] | 173.5 | 449
[18 empty] | 03110150011z | [30 empty] | 14G 1.5 | 16.2 | [12 empty] | 202.5 | 499
[18 empty] | 03110151011z | [30 empty] | 18G 1.5 | 17.8 | [12 empty] | 260 | 593
[18 empty] | 03110152011z | [30 empty] | 25G 1.5 | 19.3 | [12 empty] | 361 | 890
[18 empty] | 03110153011z | [30 empty] | 32G 1.5 | 22.1 | [12 empty] | 462.5 | 1003
[18 empty] | 03110154011z | [30 empty] | 41G 1.5 | 25.1 | [12 empty] | 592.5 | 1214
[18 empty] | 03110155011z | [30 empty] | 50G 1.5 | 26.4 | [12 empty] | 722.5 | 1636
[18 empty] | 03110156011z | [30 empty] | 3G 2.5 | 11.5 | [12 empty] | 61 | 228
[18 empty] | 03110157011z | [30 empty] | 4G 2.5 | 12.4 | [12 empty] | 82 | 290
[18 empty] | 03110158011z | [30 empty] | 5G 2.5 | 13.3 | [12 empty] | 102 | 341
[18 empty] | 03110159011z | [30 empty] | 7G 2.5 | 14.3 | [12 empty] | 142 | 394
[18 empty] | 03110160011z | [30 empty] | 12G 2.5 | 18.3 | [12 empty] | 248 | 627
[18 empty] | 03110161011z | [30 empty] | 18G 2.5 | 21.4 | [12 empty] | 378 | 892
[18 empty] | 03110162011z | [30 empty] | 25G 2.5 | 23.1 | [12 empty] | 525 | 1182
[18 empty] | 03110163011z | [30 empty] | 3G 4 | 12.7 | [12 empty] | 96 | 296
[18 empty] | 03110164011z | [30 empty] | 4G 4 | 13.7 | [12 empty] | 128 | 345
[18 empty] | 03110165011z | [30 empty] | 5G 4 | 14.9 | [12 empty] | 159.5 | 410
[18 empty] | 03110166011z | [30 empty] | 7G 4 | 16.1 | [12 empty] | 223.5 | 550
[18 empty] | 03110167011z | [30 empty] | 4G 6 | 16 | [12 empty] | 191.5 | 540
[18 empty] | 03110168011z | [30 empty] | 5G 6 | 17.3 | [12 empty] | 239.5 | 570
[18 empty] | 03110169011z | [30 empty] | 7G 6 | 18.8 | [12 empty] | 335 | 725
[18 empty] | 03110170011z | [30 empty] | 4G 10 | 18.4 | [12 empty] | 326 | 710
[18 empty] | 03110171011z | [30 empty] | 5G 10 | 20.1 | [12 empty] | 407.5 | 865
[18 empty] | 03110172011z | [30 empty] | 7G 10 | 21.9 | [12 empty] | 570.5 | 1100
[18 empty] | 03110173011z | [30 empty] | 4G 16 | 22 | [12 empty] | 543 | 1050
[18 empty] | 03110174011z | [30 empty] | 5G 16 | 24.1 | [12 empty] | 678.5 | 1280
[18 empty] | 03110175011z | [30 empty] | 4G 25 | 26.4 | [12 empty] | 844.5 | 1620
[18 empty] | 03110176011z | [30 empty] | 5G 25 | 29 | [12 empty] | 1055.5 | 1970
[18 empty] | 03110177011z | [30 empty] | 4G 35 | 30.6 | [12 empty] | 1189 | 2205
https://www.rrkabel.com/control-cable/control-cable-jz-cy | JZ-CY | ['https://www.rrkabel.com/Uploads/Products/38/ProductZoomForMoreDetailsImage/02.jpg', 'https://www.rrkabel.com/Uploads/Products/38/ProductZoomImage/03.jpg', 'https://www.rrkabel.com/Uploads/Products/112/ProductFeaturesDetails/8-8-8.png', 'https://www.rrkabel.com/Uploads/Products/112/ProductFeaturesDetails/8-8-8.png'] | ['PVC self-extinguishing and flame retardant according to EN 60332-1-2.', 'JZ-CY grey (RAL 7001) is available in oil resistant variant as JZ-CY OR. The outer sheath provided here is of special PVC TM5 to BS EN 50363 -4.1.', "For Oil Resistant sheath kindly add 'OR' after the part nos."] | [21 empty] | ['For use as a data cable in control circuits, in tool-making and machine industries as well as a signal cable in computer systems and electronics. The more usual PVC inner sheath has been removed in the cable, thus reducing the total diameter of the cables considerably and thereby reducing the bending radius, total weight etc. The dense screening assures disturbance-free transmission of all signals and impulses.'] | [5 empty] | ['Adapted to DIN VDE 0245, 0281 Part 13.'] | ['U', '0', '/ U 300 / 500V'] | ['Min. 20 GΩ x cm'] | ['Flexing -5°C to +70°C. Fixed installation -30°C to +70°C'] |  | ['Core/core 4000V. Core/screen 2000V'] | ['Bare copper, fine wire conductors, to EN 60228 Cl.5. Core insulation of special PVC TI2, EN 50363-3.Black Core with continuous white numbering to DIN VDE 0293. Green/yellow earth core in outer layer (3 cores and above).Cores stranded in layers with optimal lay-length. Plastic foil over the laid up cores.Tinned copper, braided screen, approx 85% coverage.Cable Sheath of Special PVC, TM2 to DIN/BS EN 50363-4.1. Colour grey (RAL 7001).'] | [13 empty] | ['Flexing 10 x cable ø. Fixed installation5 x cable ø']
[18 empty] | 31200201050 | [30 empty] | 2 x 0.5 | 5.8 | [12 empty] | 18.8 | 46
[18 empty] | 31200311050 | [30 empty] | 3G 0.5 | 6.1 | [12 empty] | 24.7 | 55
[18 empty] | 31200301050 | [30 empty] | 3 x 0.5 | 6.1 | [12 empty] | 24.7 | 55
[18 empty] | 31200411050 | [30 empty] | 4G 0.5 | 6.6 | [12 empty] | 29.2 | 69
[18 empty] | 31200401050 | [30 empty] | 4 x 0.5 | 6.6 | [12 empty] | 29.2 | 69
[18 empty] | 31200511050 | [30 empty] | 5G 0.5 | 7.1 | [12 empty] | 34.6 | 80
[18 empty] | 31200501050 | [30 empty] | 5 x 0.5 | 7.1 | [12 empty] | 34.6 | 80
[18 empty] | 31200711050 | [30 empty] | 7G 0.5 | 7.6 | [12 empty] | 45.1 | 99
[18 empty] | 31200701050 | [30 empty] | 7 x 0.5 | 7.6 | [12 empty] | 45.1 | 99
[18 empty] | 31201211050 | [30 empty] | 12G 0.5 | 9.8 | [12 empty] | 71.4 | 151
[18 empty] | 31201201050 | [30 empty] | 12 x 0.5 | 9.8 | [12 empty] | 71.4 | 151
[18 empty] | 31201811050 | [30 empty] | 18G 0.5 | 11.3 | [12 empty] | 100.1 | 210
[18 empty] | 31201801050 | [30 empty] | 18 x 0.5 | 11.3 | [12 empty] | 100.1 | 210
[18 empty] | 31202511050 | [30 empty] | 25G 0.5 | 12.3 | [12 empty] | 134.1 | 270
[18 empty] | 31202501050 | [30 empty] | 25 x 0.5 | 12.3 | [12 empty] | 134.1 | 270
[18 empty] | 31200201075 | [30 empty] | 2 x 0.75 | 6.3 | [12 empty] | 25 | 58
[18 empty] | 31200311075 | [30 empty] | 3G 0.75 | 6.7 | [12 empty] | 31.3 | 70
[18 empty] | 31200301075 | [30 empty] | 3 x 0.75 | 6.7 | [12 empty] | 31.3 | 70
[18 empty] | 31200411075 | [30 empty] | 4G 0.75 | 7.2 | [12 empty] | 39 | 84
[18 empty] | 31200401075 | [30 empty] | 4 x 0.75 | 7.2 | [12 empty] | 39 | 84
[18 empty] | 31200511075 | [30 empty] | 5G 0.75 | 7.8 | [12 empty] | 47.2 | 101
[18 empty] | 31200501075 | [30 empty] | 5 x 0.75 | 7.8 | [12 empty] | 47.2 | 101
[18 empty] | 31200711075 | [30 empty] | 7G 0.75 | 8.4 | [12 empty] | 62 | 126
[18 empty] | 31200701075 | [30 empty] | 7 x 0.75 | 8.4 | [12 empty] | 62 | 126
[18 empty] | 31201211075 | [30 empty] | 12G 0.75 | 10.9 | [12 empty] | 98.9 | 200
[18 empty] | 31201811075 | [30 empty] | 18G 0.75 | 12.7 | [12 empty] | 141 | 275
[18 empty] | 31202511075 | [30 empty] | 25G 0.75 | 13.8 | [12 empty] | 210.6 | 360
[18 empty] | 31202501075 | [30 empty] | 25 x 0.75 | 13.8 | [12 empty] | 210.6 | 360
[18 empty] | 31200200001 | [30 empty] | 2 x 1 | 6.7 | [12 empty] | 29.5 | 65
[18 empty] | 31200310001 | [30 empty] | 3G 1 | 7 | [12 empty] | 38.9 | 80
[18 empty] | 31200300001 | [30 empty] | 3 x 1 | 7 | [12 empty] | 38.9 | 80
[18 empty] | 31200410001 | [30 empty] | 4G 1 | 7.6 | [12 empty] | 49.1 | 100
[18 empty] | 31200400001 | [30 empty] | 4 x 1 | 7.6 | [12 empty] | 49.1 | 100
[18 empty] | 31200510001 | [30 empty] | 5G 1 | 8.3 | [12 empty] | 58.4 | 120
[18 empty] | 31200500001 | [30 empty] | 5 x 1 | 8.3 | [12 empty] | 58.4 | 120
[18 empty] | 31200710001 | [30 empty] | 7G 1 | 8.9 | [12 empty] | 77.2 | 150
[18 empty] | 31200700001 | [30 empty] | 7 x 1 | 8.9 | [12 empty] | 77.2 | 150
[18 empty] | 31201210001 | [30 empty] | 12G 1 | 11.6 | [12 empty] | 125.5 | 240
[18 empty] | 31201810001 | [30 empty] | 18G 1 | 13.5 | [12 empty] | 180 | 330
[18 empty] | 31202510001 | [30 empty] | 25G 1 | 14.7 | [12 empty] | 266.1 | 430
[18 empty] | 31200201105 | [30 empty] | 2 x 1.5 | 7.3 | [12 empty] | 39.4 | 80
[18 empty] | 31200311105 | [30 empty] | 3G 1.5 | 7.7 | [12 empty] | 51.7 | 100
[18 empty] | 31200301105 | [30 empty] | 3 x 1.5 | 7.7 | [12 empty] | 51.7 | 100
[18 empty] | 31200411105 | [30 empty] | 4G 1.5 | 8.4 | [12 empty] | 66.2 | 125
[18 empty] | 31200401105 | [30 empty] | 4 x 1.5 | 8.4 | [12 empty] | 66.2 | 125
[18 empty] | 31200511105 | [30 empty] | 5G 1.5 | 9.1 | [12 empty] | 80.9 | 150
[18 empty] | 31200501105 | [30 empty] | 5 x 1.5 | 9.1 | [12 empty] | 80.9 | 150
[18 empty] | 31200711105 | [30 empty] | 7G 1.5 | 9.9 | [12 empty] | 108 | 190
[18 empty] | 31200701105 | [30 empty] | 7 x 1.5 | 9.9 | [12 empty] | 108 | 190
[18 empty] | 31201211105 | [30 empty] | 12G 1.5 | 12.9 | [12 empty] | 175.1 | 285
[18 empty] | 31201811105 | [30 empty] | 18G 1.5 | 15.1 | [12 empty] | 276 | 435
[18 empty] | 31202511105 | [30 empty] | 25G 1.5 | 16.7 | [12 empty] | 377.6 | 590
[18 empty] | 31203411105 | [30 empty] | 34G 1.5 | 20.4 | [12 empty] | 488.3 | 800
[18 empty] | 31200311205 | [30 empty] | 3G 2.5 | 9.1 | [12 empty] | 80.9 | 150
[18 empty] | 31200411205 | [30 empty] | 4G 2.5 | 10 | [12 empty] | 102.9 | 190
[18 empty] | 31200511205 | [30 empty] | 5G 2.5 | 10.9 | [12 empty] | 125 | 220
[18 empty] | 31200711205 | [30 empty] | 7G 1.5 | 9.9 | [12 empty] | 168.4 | 260
[18 empty] | 31201211205 | [30 empty] | 12G 2.5 | 15.8 | [12 empty] | 301 | 475
[18 empty] | 31201811205 | [30 empty] | 18G 2.5 | 18.5 | [12 empty] | 433.3 | 654
[18 empty] | 31202511205 | [30 empty] | 25G 2.5 | 20.3 | [12 empty] | 588 | 878
[18 empty] | 31200410004 | [30 empty] | 4G 4 | 11.6 | [12 empty] | 153.4 | 250.4
[18 empty] | 31200710004 | [30 empty] | 7G 4 | 13.5 | [12 empty] | 256.1 | 400
[18 empty] | 31200410006 | [30 empty] | 4G 6 | 13.4 | [12 empty] | 222.7 | 360
[18 empty] | 31200710006 | [30 empty] | 7G 6 | 16.2 | [12 empty] | 396.3 | 590
[18 empty] | 31200410010 | [30 empty] | 4G 10 | 15.9 | [12 empty] | 384.1 | 560
[18 empty] | 31200510010 | [30 empty] | 5G 10 | 17.5 | [12 empty] | 475.8 | 711
[18 empty] | 31200410016 | [30 empty] | 4G 16 | 19.3 | [12 empty] | 616.3 | 840
[18 empty] | 31200510016 | [30 empty] | 5G 16 | 21.4 | [12 empty] | 760.4 | 1050
[18 empty] | 31200410025 | [30 empty] | 4G 25 | 23.6 | [12 empty] | 937.4 | 1300
[18 empty] | 31200510025 | [30 empty] | 5G 25 | 26.1 | [12 empty] | 1160 | 1605
[18 empty] | 31200410035 | [30 empty] | 4G 35 | 28 | [12 empty] | 1312 | 1804
https://www.rrkabel.com/ProductsDetails/index/39 | JZ – BLACK 0.6/1 kV | ['https://www.rrkabel.com/Uploads/Products/39/ProductZoomForMoreDetailsImage/JZ-BK-0.6-1-KV.jpg', 'https://www.rrkabel.com/Uploads/Products/39/ProductZoomImage/7.png', 'https://www.rrkabel.com/Uploads/Products/115/ProductFeaturesDetails/7-7-7.png', 'https://www.rrkabel.com/Uploads/Products/115/ProductFeaturesDetails/7-7-7.png'] | [22 empty] | ['Wiring cable in tool machinery, conveyor belts and production lines, plant engineering, Industrial machinery, air conditioning, steel production plants and rolling mills.'] | ['Nominal Voltage : U0 / U 0.6 / 1kV Insulation Resistance : Min. 20 GΩ x cm Temperature Range : Flexing -5°C to +70°C. Fixed installation -30°C to +70°C Minimum Bending Radius : Flexing 15 x cable ø. Fixed installation 4 x cable ø Test Voltage : 4000V Breakdown Voltage : Min. 8000V'] |  |  |  |  | ['Adapted to DIN VDE 0262, DIN VDE 0281 Part 13 with increased insulation thickness for 1 kV.'] | [5 empty] | ['Bare copper, fine wire conductors, as per EN60228 Cl. 5. Special PVC core insulation TI2, to EN 50363-3. Black Core with continuous white numbering to DIN VDE 0293. Green/yellow earth core in outer layer (3 cores and above). Cores stranded in layers with optimal lay-length. Special PVC outer sheath TM2, to EN 50363-4-1. Colour Black (RAL 9005).'] | ['PVC self-extinguishing and flame retardant according to IEC 60332-1-2. UV & weather resistant according to ASTM G 154. Ozone resistant according to EN 50396.']
[18 empty] | 31300201075 | [30 empty] | 2 x 0.75 | 8.3 | [12 empty] | 13 | 90
[18 empty] | 31300311075 | [30 empty] | 3G 0.75 | 8.7 | [12 empty] | 19.6 | 103
[18 empty] | 31300301075 | [30 empty] | 3 x 0.75 | 8.7 | [12 empty] | 19.6 | 103
[18 empty] | 31300411075 | [30 empty] | 4G 0.75 | 9.2 | [12 empty] | 26.1 | 119
[18 empty] | 31300511075 | [30 empty] | 5G 0.75 | 9.9 | [12 empty] | 32.6 | 139
[18 empty] | 31300711075 | [30 empty] | 7G 0.75 | 10.7 | [12 empty] | 45.6 | 169
[18 empty] | 31301211075 | [30 empty] | 12G 0.75 | 13.4 | [12 empty] | 78.2 | 271
[18 empty] | 31301811075 | [30 empty] | 18G 0.75 | 15.6 | [12 empty] | 117.3 | 377
[18 empty] | 31304111075 | [30 empty] | 41G 0.75 | 23.2 | [12 empty] | 267.3 | 840
[18 empty] | 31300200001 | [30 empty] | 2 x 1 | 8.6 | [12 empty] | 17.4 | 99
[18 empty] | 31300310001 | [30 empty] | 3G 1 | 9 | [12 empty] | 26.1 | 114.4
[18 empty] | 31300300001 | [30 empty] | 3 x 1 | 9 | [12 empty] | 26.1 | 114.4
[18 empty] | 31300410001 | [30 empty] | 4G 1 | 9.6 | [12 empty] | 34.8 | 134.5
[18 empty] | 31300400001 | [30 empty] | 4 x 1 | 9.6 | [12 empty] | 34.8 | 134.5
[18 empty] | 31300510001 | [30 empty] | 5G 1 | 10.4 | [12 empty] | 43.5 | 160.1
[18 empty] | 31300500001 | [30 empty] | 5 x 1 | 10.4 | [12 empty] | 43.5 | 160.1
[18 empty] | 31300710001 | [30 empty] | 7G 1 | 11.4 | [12 empty] | 60.8 | 199.8
[18 empty] | 31301210001 | [30 empty] | 12G 1 | 14.5 | [12 empty] | 104.3 | 328.2
[18 empty] | 31301810001 | [30 empty] | 18G 1 | 16.5 | [12 empty] | 156.5 | 443.2
[18 empty] | 31302510001 | [30 empty] | 25G 1 | 19.7 | [12 empty] | 217.3 | 626.9
[18 empty] | 31303410001 | [30 empty] | 34G 1 | 22.5 | [12 empty] | 295.5 | 828
[18 empty] | 31304110001 | [30 empty] | 41G 1 | 24.4 | [12 empty] | 356.4 | 981.3
[18 empty] | 31300201105 | [30 empty] | 2 x 1.5 | 9.6 | [12 empty] | 25.5 | 127
[18 empty] | 31300311105 | [30 empty] | 3G 1.5 | 10.1 | [12 empty] | 38.2 | 149
[18 empty] | 31300301105 | [30 empty] | 3 x 1.5 | 10.1 | [12 empty] | 38.2 | 149
[18 empty] | 31300411105 | [30 empty] | 4G 1.5 | 10.8 | [12 empty] | 50.9 | 176
[18 empty] | 31300511105 | [30 empty] | 5G 1.5 | 11.7 | [12 empty] | 63.7 | 210
[18 empty] | 31300711105 | [30 empty] | 7G 1.5 | 12.6 | [12 empty] | 89.1 | 257
[18 empty] | 31301211105 | [30 empty] | 12G 1.5 | 16.1 | [12 empty] | 152.8 | 425
[18 empty] | 31301411105 | [30 empty] | 14G 1.5 | 17 | [12 empty] | 178.3 | 481
[18 empty] | 31301811105 | [30 empty] | 18G 1.5 | 18.8 | [12 empty] | 229.2 | 598
[18 empty] | 31302511105 | [30 empty] | 25G 1.5 | 21.7 | [12 empty] | 318.3 | 807
[18 empty] | 31303411105 | [30 empty] | 34G 1.5 | 24.9 | [12 empty] | 407.4 | 1053
[18 empty] | 31305011105 | [30 empty] | 50G 1.5 | 29.8 | [12 empty] | 636.6 | 1553
[18 empty] | 31300211205 | [30 empty] | 2G 2.5 | 10.8 | [12 empty] | 42.4 | 169
[18 empty] | 31300311205 | [30 empty] | 3G 2.5 | 11.3 | [12 empty] | 63.7 | 200
[18 empty] | 31300411205 | [30 empty] | 4G 2.5 | 12.2 | [12 empty] | 84.9 | 242
[18 empty] | 31300511205 | [30 empty] | 5G 2.5 | 13.3 | [12 empty] | 106.1 | 292
[18 empty] | 31300711205 | [30 empty] | 7G 2.5 | 14.4 | [12 empty] | 148.5 | 363
[18 empty] | 31301211205 | [30 empty] | 12G 2.5 | 18.7 | [12 empty] | 254.6 | 615
[18 empty] | 31301411205 | [30 empty] | 14G 2.5 | 19.8 | [12 empty] | 297.1 | 699
[18 empty] | 31301811205 | [30 empty] | 18G 2.5 | 22 | [12 empty] | 382 | 876
[18 empty] | 31302511205 | [30 empty] | 25G 2.5 | 25.8 | [12 empty] | 530.5 | 1210
[18 empty] | 31300410004 | [30 empty] | 4G 4 | 13.8 | [12 empty] | 135 | 332
[18 empty] | 31300510004 | [30 empty] | 5G 4 | 15.1 | [12 empty] | 168.7 | 403
[18 empty] | 31300710004 | [30 empty] | 7G 4 | 16.4 | [12 empty] | 236.2 | 507
[18 empty] | 31300410006 | [30 empty] | 4G 6 | 15.1 | [12 empty] | 202.4 | 432
[18 empty] | 31300510006 | [30 empty] | 5G 6 | 16.8 | [12 empty] | 253.1 | 537
[18 empty] | 31300710006 | [30 empty] | 7G 6 | 18.2 | [12 empty] | 354.3 | 679
[18 empty] | 31300410010 | [30 empty] | 4G 10 | 18.7 | [12 empty] | 344.7 | 692
[18 empty] | 31300510010 | [30 empty] | 5G 10 | 20.7 | [12 empty] | 430.8 | 855
[18 empty] | 31300410016 | [30 empty] | 4G 16 | 21.3 | [12 empty] | 574.1 | 1006
[18 empty] | 31300510016 | [30 empty] | 5G 16 | 23.6 | [12 empty] | 717.7 | 1245
[18 empty] | 31300710016 | [30 empty] | 7G 16 | 26.2 | [12 empty] | 1004.7 | 1637
[18 empty] | 31300410025 | [30 empty] | 4G 25 | 26.2 | [12 empty] | 893.1 | 1542
[18 empty] | 31300510025 | [30 empty] | 5G 25 | 29 | [12 empty] | 1116.3 | 1908
[18 empty] | 31300410035 | [30 empty] | 4G 35 | 29.1 | [12 empty] | 1257.6 | 2035
[18 empty] | 31300510035 | [30 empty] | 5G 35 | 32.5 | [12 empty] | 1572 | 2541
[18 empty] | 31300410050 | [30 empty] | 4G 50 | 35.6 | [12 empty] | 1804.4 | 2980
[18 empty] | 31300410070 | [30 empty] | 4G 70 | 40.7 | [12 empty] | 2549.7 | 4058
[18 empty] | 31300410095 | [30 empty] | 4G 95 | 46.8 | [12 empty] | 3399.7 | 5389
[18 empty] | 31300410120 | [30 empty] | 4G 120 | 53.5 | [12 empty] | 4306.2 | 6926
https://www.rrkabel.com/control-cable/control-cable-jz-ycy-black-0-61-kv | JZ-YCY BLACK 0.6/1kV | ['https://www.rrkabel.com/Uploads/Products/40/ProductZoomForMoreDetailsImage/02.jpg', 'https://www.rrkabel.com/Uploads/Products/40/ProductZoomImage/03.jpg', 'https://www.rrkabel.com/Uploads/Products/118/ProductFeaturesDetails/6-6-6.png', 'https://www.rrkabel.com/Uploads/Products/118/ProductFeaturesDetails/6-6-6.png'] | [22 empty] | ['Wiring cable in tool machinery, conveyor belts and production lines, plant engineering, Industrial machinery, air conditioning, steel production plants and rolling mills. The dense coverage of copper screening offers EMI compliance.'] | [5 empty] | ['Adapted to DIN VDE 0262/12.95 and 0281 Part 13 with insulation thickness for 1 kV type.'] | ['UO / U 0.6 / 1kV'] | ['Min. 20 GΩ x cm'] | ['Flexing -5°C to +70°C. Fixed installation -30°C to +70°C Minimum Bending Radius : Flexing 20 x cable ø. Fixed installation 6 x cable ø Test Voltage : 4000V'] |  |  | ['Bare copper, fine wire conductors, as per DIN VDE 0295 Cl. 5. Special PVC core insulation TI2, to EN 50363-3.Black Core with continuous white numbering to DIN VDE 0293. Green/yellow earth core in outer layer (3 cores and above).Cores stranded in layers with optimal lay-length. PVC inner jacket, Black color.Tinned copper, braided screen, approx 85% coverage. Special PVC outer sheath TM2, to EN 50363-4.1.Colour Black (RAL 9005).'] | ['PVC self-extinguishing and flame retardant according to IEC 60332-1-2. UV & weather resistant according to ASTM G 154.Ozone resistant according to EN 50396.']
[54 empty] | 31400201075 |  | 10.5 | 34.4 | 150 | 2 x 0.75
[54 empty] | 31400311075 |  | 10.9 | 40.9 | 165 | 3G 0.75
[54 empty] | 31400301075 |  | 10.9 | 40.9 | 165 | 3 x 0.75
[54 empty] | 31400411075 |  | 11.4 | 49.8 | 185 | 4G 0.75
[54 empty] | 31400401075 |  | 11.4 | 49.8 | 185 | 4 x 0.75
[54 empty] | 31400511075 |  | 12.1 | 60 | 212 | 5G 0.75
[54 empty] | 31400501075 |  | 12.1 | 60 | 212 | 5 x 0.75
[54 empty] | 31400711075 |  | 12.9 | 74.9 | 247 | 7G 0.75
[54 empty] | 31400701075 |  | 12.9 | 74.9 | 247 | 7 x 0.75
[54 empty] | 31401211075 |  | 15.8 | 138.7 | 389 | 12G 0.75
[54 empty] | 31401201075 |  | 15.8 | 138.7 | 389 | 12 x 0.75
[54 empty] | 31401811075 |  | 18 | 185.5 | 510 | 18G 0.75
[54 empty] | 31402511075 |  | 20.7 | 243.4 | 676 | 25G 0.75
[54 empty] | 31400200001 |  | 10.8 | 38.9 | 161 | 2 x 1
[54 empty] | 31400310001 |  | 11.2 | 50.4 | 181 | 3G 1
[54 empty] | 31400300001 |  | 11.2 | 50.4 | 181 | 3 x 1
[54 empty] | 31400410001 |  | 11.8 | 59.4 | 203 | 4G 1
[54 empty] | 31400400001 |  | 11.8 | 59.4 | 203 | 4 x 1
[54 empty] | 31400510001 |  | 12.6 | 70.8 | 235 | 5G 1
[54 empty] | 31400710001 |  | 13.3 | 107.3 | 281 | 7G 1
[54 empty] | 31401210001 |  | 16.4 | 165.7 | 433 | 12G 1
[54 empty] | 31401810001 |  | 18.7 | 233.9 | 581 | 18G 1
[54 empty] | 31402510001 |  | 21.6 | 304.6 | 771 | 25G 1
[54 empty] | 31400201105 |  | 11.8 | 50.3 | 196 | 2 x 1.5
[54 empty] | 31400311105 |  | 12.3 | 62.4 | 219 | 3G 1.5
[54 empty] | 31400301105 |  | 12.3 | 62.4 | 219 | 3 x 1.5
[54 empty] | 31400411105 |  | 13 | 77.9 | 252 | 4G 1.5
[54 empty] | 31400401105 |  | 13 | 77.9 | 252 | 4 x 1.5
[54 empty] | 31400511105 |  | 13.9 | 93.4 | 293 | 5G 1.5
[54 empty] | 31400711105 |  | 15 | 143.3 | 366 | 7G 1.5
[54 empty] | 31401211105 |  | 18.7 | 222.3 | 572 | 12G 1.5
[54 empty] | 31401811105 |  | 21.8 | 309 | 785 | 18G 1.5
[54 empty] | 31402511105 |  | 25.1 | 411.1 | 1045 | 25G 1.5
[54 empty] | 31400311205 |  | 13.5 | 91.9 | 279 | 3G 2.5
[54 empty] | 31400411205 |  | 14.6 | 137.7 | 349 | 4G 2.5
[54 empty] | 31400511205 |  | 15.7 | 158.8 | 403 | 5G 2.5
[54 empty] | 31400711205 |  | 17 | 209 | 493 | 7G 2.5
[54 empty] | 31401211205 |  | 21.7 | 333.7 | 802 | 12G 2.5
[54 empty] | 31400410004 |  | 17 | 195 | 483 | 4G 4
[54 empty] | 31400510004 |  | 18.6 | 235 | 581 | 5G 4
[54 empty] | 31400710004 |  | 20.1 | 308 | 704 | 7G 4
[54 empty] | 31400410006 |  | 18.2 | 269 | 590 | 4G 6
[54 empty] | 31400510006 |  | 19.7 | 327 | 706 | 5G 6
[54 empty] | 31400710006 |  | 21.8 | 437 | 895 | 7G 6
[54 empty] | 31400410010 |  | 21.7 | 425.5 | 880 | 4G 10
[54 empty] | 31400510010 |  | 23 | 521.9 | 1027 | 5G 10
[54 empty] | 31400410016 |  | 24.3 | 666.5 | 1219 | 4G 16
[54 empty] | 31400510016 |  | 26.7 | 820.1 | 1487 | 5G 16
[54 empty] | 31400410025 |  | 29.8 | 1007 | 1844 | 4G 25
[54 empty] | 31400510025 |  | 31.6 | 1242.1 | 2167 | 5G 25
[54 empty] | 31400410035 |  | 32.7 | 1384.4 | 2368 | 4G 35
[54 empty] | 31400410050 |  | 39.6 | 2032.2 | 3471 | 4G 50
[54 empty] | 31400410070 |  | 44.5 | 2824.2 | 4602 | 4G 70
[54 empty] | 31400410095 |  | 51 | 3706.2 | 6050 | 4G 95
[54 empty] | 31400410120 |  | 58.1 | 4650.3 | 7727 | 4G 120
https://www.rrkabel.com/control-cable/control-cable-oz-eb | OZ-EB | ['https://www.rrkabel.com/Uploads/Products/41/ProductZoomForMoreDetailsImage/02.jpg', 'https://www.rrkabel.com/Uploads/Products/41/ProductZoomImage/03.jpg', 'https://www.rrkabel.com/Uploads/Products/121/ProductFeaturesDetails/sheath-29.png', 'https://www.rrkabel.com/Uploads/Products/121/ProductFeaturesDetails/sheath-29.png'] | [22 empty] | ['These cables are used for intrinsically safe circuits. For hazard prone areas cables with blue sheath are used for controlling and measuring requirements. These installations are not earthed and require a seperate power circuit.'] | [5 empty] | ['Adapted to DIN EN 60079-14, VDE 0165 Part 1.'] | ['U', 'O', '/ U 300 / 500V.'] | ['Min. 20 GΩ x cm'] | ['Flexing -5°C to +70°C. Fixed installation -30°C to +70°C'] |  | ['3000V'] | ['Bare copper, fine wire conductors, to EN 60228 Cl.5. Core insulation of special PVC TI2 EN 50363-3.Black core with continuous white numbering according to DIN VDE 0293. Green/Yellow earth core in outer layer (3 cores and above).Cores stranded in layers with optimal lay-length.Outer sheath of special PVC, TM2 to DIN/BS EN 50363-4.1.Colour Blue (RAL 5015).'] | ['PVC self-extinguishing and flame retardant according to EN 60332-1-2.'] | [12 empty] | ['Flexing 15 x cable ø. Fixed installation 4 x cable ø']
[54 empty] | 31500201075 |  | 5.3 | 4.5 | 44 | 2 x 0.75
[54 empty] | 31500301075 |  | 5.6 | 1.5 | 54 | 3 x 0.75
[54 empty] | 31500401075 |  | 6.1 | 8.5 | 66 | 4 x 0.75
[54 empty] | 31500501075 |  | 6.9 | 6 | 85 | 5 x 0.75
[54 empty] | 31501211075 |  | 10.1 | 85.5 | 190 | 12G 0.75
[54 empty] | 31501811075 |  | 11.9 | 128 | 273 | 18G 0.75
[54 empty] | 31502511075 |  | 14.6 | 178 | 396 | 25G 0.75
[54 empty] | 31500200001 |  | 5.6 | 19 | 52 | 2 x 1
[54 empty] | 31500300001 |  | 6 | 28.5 | 66 | 3 x 1
[54 empty] | 31500400001 |  | 6.8 | 38 | 86 | 4 x 1
[54 empty] | 31500500001 |  | 7.5 | 47.5 | 104 | 5 x 1
[54 empty] | 31500700001 |  | 8.9 | 66.5 | 148 | 7 x 1
[54 empty] | 31501200001 |  | 11.1 | 114 | 239 | 12 x 1
[54 empty] | 31501800001 |  | 13.2 | 171 | 346 | 18 x 1
[54 empty] | 31500201105 |  | 6.3 | 29 | 69 | 2 x 1.5
[54 empty] | 31500301105 |  | 6.7 | 43.5 | 87 | 3 x 1.5
[54 empty] | 31500401105 |  | 7.3 | 58 | 109 | 4 x 1.5
[54 empty] | 31500501105 |  | 8.2 | 72.5 | 137 | 5 x 1.5
[54 empty] | 31500311105 |  | 6.7 | 43.5 | 87 | 3 G 1.5
[54 empty] | 31500411105 |  | 7.3 | 58 | 109 | 4 G 1.5
[54 empty] | 31500511105 |  | 8.2 | 72.5 | 137 | 5 G 1.5
[54 empty] | 31501811105 |  | 14.5 | 260 | 455 | 18G 1.5
[54 empty] | 31502511105 |  | 17.2 | 361 | 637 | 25G 1.5
https://www.rrkabel.com/control-cable/control-cable-oz-eb-cy | OZ-EB CY | ['https://www.rrkabel.com/Uploads/Products/42/ProductZoomForMoreDetailsImage/02.jpg', 'https://www.rrkabel.com/Uploads/Products/42/ProductZoomImage/03.jpg', 'https://www.rrkabel.com/Uploads/Products/124/ProductFeaturesDetails/sheath-28.png', 'https://www.rrkabel.com/Uploads/Products/124/ProductFeaturesDetails/sheath-28.png'] | [22 empty] | ['These cables are used for intrinsically safe circuits. For hazard prone areas cables with blue sheath are used for controlling and measuring requirements. These installations are not earthed and require a seperate power circuit. Tinned copper braid screen ensures disturbance free transmission of data and signals.'] | [5 empty] | ['Adapted to DIN EN 60079-14: VDE 0165 Part 1.'] | ['U', 'O', '/ U 300 / 500V.'] | ['Min. 20 GΩ x cm'] | ['Flexing -5°C to +70°C. Fixed installation -30°C to +70°C'] |  | ['3000V'] | ['Bare copper, fine wire conductors, to DIN/BS EN 60228 Cl.5. Core insulation of special PVC TI2 EN 50363-3.Black core with continuous white numbering according to DIN VDE 0293. Cores stranded in layers with optimal lay-length.Plastic foil over the laid up cores.Tinned-copper braided screen, approx. 85% coverage. Outer sheath of special PVC, TM2 to DIN/BS EN 50363-4.1. Colour Blue (RAL 5015).'] | ['PVC self-extinguishing and flame retardant according to IEC 60332-1-2.'] | [12 empty] | ['Flexing 20 x cable ø. Fixed installation 6 x cable ø'] | [13 empty] | ['core to core (approx.) - 140 nF/km', 'core to screen (approx.) - 185 nF/km']
[54 empty] | 31600201075 |  | 6.2 | 25 | 53.2 | 2 x 0.75
[54 empty] | 31600201075 |  | 6.5 | 31.3 | 64 | 3 x 0.75
[54 empty] | 31600201075 |  | 7 | 39 | 77 | 4 x 0.75
[54 empty] | 31600201075 |  | 7 | 39 | 77 | 4G 0.75
[54 empty] | 31600201075 |  | 7.7 | 47.2 | 93.4 | 5 x 0.75
[54 empty] | 31600201075 |  | 8.3 | 62 | 116.4 | 7 x 0.75
[54 empty] | 31600201075 |  | 10.9 | 98.9 | 189.7 | 12 x 0.75
[54 empty] | 31600201075 |  | 12.7 | 141 | 265 | 18 x 0.75
[54 empty] | 31600201075 |  | 14.8 | 210.6 | 363.6 | 25 x 0.75
[54 empty] | 31600201075 |  | 6.5 | 29.5 | 59.7 | 2 x 1
[54 empty] | 31600201075 |  | 6.8 | 38.9 | 73.6 | 3 x 1
[54 empty] | 31600201075 |  | 7.3 | 49.1 | 89 | 4 x 1
[54 empty] | 31600201075 |  | 8.1 | 58.4 | 108.1 | 5 x 1
[54 empty] | 31600201075 |  | 8.8 | 77.2 | 136.8 | 7 x 1
[54 empty] | 31600201075 |  | 11.5 | 125.5 | 223.3 | 12 x 1
[54 empty] | 31600201075 |  | 13.9 | 180 | 328.9 | 18 x 1
[54 empty] | 31600201075 |  | 15.9 | 266.1 | 439.8 | 25 x 1
[54 empty] | 31600201075 |  | 7.1 | 39.4 | 73.9 | 2 x 1.5
[54 empty] | 31600201075 |  | 7.5 | 51.7 | 92.7 | 3 x 1.5
[54 empty] | 31600201075 |  | 8.2 | 66.2 | 115.9 | 4 x 1.5
[54 empty] | 31600201075 |  | 8.9 | 80.9 | 138.7 | 5 x 1.5
[54 empty] | 31600201075 |  | 9.9 | 108 | 182.3 | 7 x 1.5
[54 empty] | 31600201075 |  | 13 | 175.1 | 298 | 12 x 1.5
[54 empty] | 31600201075 |  | 15.6 | 276 | 450.8 | 18 x 1.5
[54 empty] | 31600201075 |  | 17.9 | 377.6 | 596.4 | 25 x 1.5
https://www.rrkabel.com/control-cable/control-cable-jb-h | JB-H | ['https://www.rrkabel.com/Uploads/Products/43/ProductZoomForMoreDetailsImage/02.jpg', 'https://www.rrkabel.com/Uploads/Products/43/ProductZoomImage/03.jpg', 'https://www.rrkabel.com/Uploads/Products/127/ProductFeaturesDetails/3-3-3.png', 'https://www.rrkabel.com/Uploads/Products/127/ProductFeaturesDetails/3-3-3.png'] | [22 empty] | ['Halogen-free cables for airports railway station, plant engineering and Industrial machinery'] | [5 empty] | ['Adapted to EN 50525-3-11'] | ['U', 'O', '/ U 450 / 750V'] |  | ['Flexing -15°C to +70°C. Fixed installation -30°C to +70°C'] |  |  | ['Bare copper, fine wire conductors, to EN 60228 Cl. 5.Core insulation of halogen-free compound TI6 to EN 50363-7.Colour coded to DIN VDE 0293-308 (Refer Appendix Table No. 1-1).Green/Yellow earth core in outer layer.Cores stranded in layers with optimal lay-length.Halogen-Free sheath compound TM7, to EN 50363-8.Sheath colour grey (RAL 7001).'] | ['Flame retardant to IEC 60332-1-2.No flame propagation according to IEC 60332-3-24 (flame spread on Vertical cable or wire bundle).Halogen free according to IEC 60754-1.Corrosive gas evolution to IEC 60754-2.'] | [12 empty] | ['Flexing approx. 15 x cable ø. Fixed installation approx. 4 x cable ø']
[54 empty] | 31700311105 |  | 8.2 | 38.2 | 110 | 3 G 1.5
[54 empty] | 31700411105 |  | 8.9 | 50.9 | 135 | 4 G 1.5
[54 empty] | 31700511105 |  | 10 | 63.7 | 169 | 5 G 1.5
[54 empty] | 31700311205 |  | 10 | 63.7 | 169 | 3G 2.5
[54 empty] | 31700411205 |  | 10.9 | 84.9 | 209 | 4G 2.5
[54 empty] | 31700511205 |  | 12 | 106.1 | 256 | 5G 2.5
[54 empty] | 31700310004 |  | 11.2 | 101.2 | 231 | 3G 4
[54 empty] | 31700410004 |  | 12.5 | 135 | 295 | 4G 4
[54 empty] | 31700510004 |  | 13.9 | 168.7 | 366 | 5G 4
[54 empty] | 31700410006 |  | 14 | 202.4 | 398 | 4G 6
[54 empty] | 31700510006 |  | 15.5 | 253.1 | 492 | 5G 6
[54 empty] | 31700410010 |  | 17.4 | 344.7 | 642 | 4G 10
[54 empty] | 31700510010 |  | 19.4 | 430.8 | 800 | 5G 10
[54 empty] | 31700410016 |  | 20.2 | 574.1 | 959 | 4G 16
[54 empty] | 31700510016 |  | 22.5 | 717.7 | 1194 | 5G 16
[54 empty] | 31700410025 |  | 25.1 | 893.1 | 1486 | 4G 25
[54 empty] | 31700510025 |  | 28.1 | 1116.3 | 1860 | 5G 25
[54 empty] | 31700410035 |  | 28.6 | 1257.6 | 2013 | 4G 35
[54 empty] | 31700510035 |  | 32.1 | 1572 | 2525 | 5G 35
[54 empty] | 31700410050 |  | 33.9 | 1804.4 | 2860 | 4G 50
[54 empty] | 31700410070 |  | 39.2 | 2549.7 | 3940 | 4G 70
[54 empty] | 31700410095 |  | 44.8 | 3399.7 | 5205 | 4G 95
[54 empty] | 31700410120 |  | 50.3 | 4306.2 | 6579 | 4G 120
https://www.rrkabel.com/control-cable/control-cable-jz-h | JZ-H | ['https://www.rrkabel.com/Uploads/Products/44/ProductZoomForMoreDetailsImage/02.jpg', 'https://www.rrkabel.com/Uploads/Products/44/ProductZoomImage/03.jpg', 'https://www.rrkabel.com/Uploads/Products/130/ProductFeaturesDetails/2-2-2.png', 'https://www.rrkabel.com/Uploads/Products/130/ProductFeaturesDetails/2-2-2.png'] | [22 empty] | ['Halogen-free cables for airports railway station, plant engineering and Industrial machinery, in EMC sensitive instruments'] | [5 empty] | ['Adapted to EN 50525-3-11.'] | ['U', 'O', '/ U 300 / 500V'] |  | ['Flexing -15°C to +70°C. Fixed installation -30°C to +70°C'] |  |  | ['Bare copper, fine wire conductors, to EN 60228 Cl. 5.Core insulation of halogen-free compound TI6 to EN 50363-7. Black colour with white numbers DIN VDE 0293.Green/Yellow earth core in outer layer.Cores stranded in layers with optimal lay-length. Halogen-free sheath compound TM7, to EN 50363-8. Sheath colour grey (RAL 7001).'] | ['Flame retardant to IEC 60332-1-2.No flame propagation according to IEC 60332-3-24 (flame spread on Vertical cable or wire bundle). Halogen free according to IEC 60754-1.Corrosive gas evolution to IEC 60754-2.'] | [12 empty] | ['Flexing approx. 10 x cable ø. Fixed installation approx. 4 x cable ø']
[18 empty] | 31800201050 | [30 empty] | 2 x 0.5 | 4.8 | [12 empty] | 9.5 | 35
[18 empty] | 31800311050 | [30 empty] | 3G 0.5 | 5.1 | [12 empty] | 14 | 42
[18 empty] | 31800301050 | [30 empty] | 3 x 0.5 | 5.1 | [12 empty] | 14.2 | 43
[18 empty] | 31800411050 | [30 empty] | 4G 0.5 | 5.5 | [12 empty] | 19 | 52
[18 empty] | 31800401050 | [30 empty] | 4 x 0.5 | 5.5 | [12 empty] | 19 | 52
[18 empty] | 31800511050 | [30 empty] | 5G 0.5 | 6 | [12 empty] | 24 | 62
[18 empty] | 31800711050 | [30 empty] | 7G 0.5 | 6.6 | [12 empty] | 33.5 | 81
[18 empty] | 31801211050 | [30 empty] | 12G 0.5 | 8.7 | [12 empty] | 57 | 141
[18 empty] | 31800201075 | [30 empty] | 2 x 0.75 | 5.3 | [12 empty] | 14.5 | 45
[18 empty] | 31800311075 | [30 empty] | 3G 0.75 | 5.6 | [12 empty] | 21.5 | 55
[18 empty] | 31800301075 | [30 empty] | 3 x 0.75 | 5.6 | [12 empty] | 21.5 | 55
[18 empty] | 31800411075 | [30 empty] | 4G 0.75 | 6.2 | [12 empty] | 28.5 | 67
[18 empty] | 31800401075 | [30 empty] | 4 x 0.75 | 6.2 | [12 empty] | 28.5 | 67
[18 empty] | 31800511075 | [30 empty] | 5G 0.75 | 6.8 | [12 empty] | 36 | 86
[18 empty] | 31800501075 | [30 empty] | 5 x 0.75 | 6.8 | [12 empty] | 36 | 86
[18 empty] | 31800711075 | [30 empty] | 7G 0.75 | 7.4 | [12 empty] | 50 | 109
[18 empty] | 31800701075 | [30 empty] | 7 x 0.75 | 7.4 | [12 empty] | 50 | 109
[18 empty] | 31800911075 | [30 empty] | 9G 0.75 | 9 | [12 empty] | 64 | 165
[18 empty] | 31801211075 | [30 empty] | 12G 0.75 | 9.8 | [12 empty] | 85.5 | 192
[18 empty] | 31801811075 | [30 empty] | 18G 0.75 | 11.5 | [12 empty] | 128 | 275
[18 empty] | 31802511075 | [30 empty] | 25G 0.75 | 12.6 | [12 empty] | 178 | 400
[18 empty] | 31800200001 | [30 empty] | 2 x 1 | 5.6 | [12 empty] | 19 | 53
[18 empty] | 31800310001 | [30 empty] | 3G 1 | 6 | [12 empty] | 28.5 | 66
[18 empty] | 31800300001 | [30 empty] | 3 x 1 | 6 | [12 empty] | 28.5 | 66
[18 empty] | 31800410001 | [30 empty] | 4G 1 | 6.6 | [12 empty] | 38 | 87
[18 empty] | 31800400001 | [30 empty] | 4 x 1 | 6.6 | [12 empty] | 38 | 87
[18 empty] | 31800510001 | [30 empty] | 5G 1 | 7.2 | [12 empty] | 47.5 | 105
[18 empty] | 31800710001 | [30 empty] | 7G 1 | 7.9 | [12 empty] | 66.5 | 149
[18 empty] | 31800810001 | [30 empty] | 8G 1 | 8.9 | [12 empty] | 76 | 175
[18 empty] | 31801210001 | [30 empty] | 12G 1 | 10.4 | [12 empty] | 114 | 241
[18 empty] | 31801410001 | [30 empty] | 14G 1 | 11 | [12 empty] | 133 | 274
[18 empty] | 31801810001 | [30 empty] | 18G 1 | 12.3 | [12 empty] | 171 | 349
[18 empty] | 31802510001 | [30 empty] | 25G 1 | 13.5 | [12 empty] | 237.5 | 508
[18 empty] | 31804110001 | [30 empty] | 41G 1 | 18.2 | [12 empty] | 389 | 782
[18 empty] | 31800201105 | [30 empty] | 2 x 1.5 | 6.3 | [12 empty] | 25.5 | 67
[18 empty] | 31800311105 | [30 empty] | 3G 1.5 | 6.7 | [12 empty] | 38.2 | 84
[18 empty] | 31800301105 | [30 empty] | 3 x 1.5 | 6.7 | [12 empty] | 38.2 | 84
[18 empty] | 31800411105 | [30 empty] | 4G 1.5 | 7.3 | [12 empty] | 50.9 | 105
[18 empty] | 31800511105 | [30 empty] | 5G 1.5 | 8 | [12 empty] | 63.7 | 132
[18 empty] | 31800711105 | [30 empty] | 7G 1.5 | 8.8 | [12 empty] | 89.1 | 169
[18 empty] | 31800811105 | [30 empty] | 8G 1.5 | 9.9 | [12 empty] | 101.9 | 216
[18 empty] | 31800911105 | [30 empty] | 9G 1.5 | 10.8 | [12 empty] | 114.6 | 250
[18 empty] | 31801211105 | [30 empty] | 12G 1.5 | 11.7 | [12 empty] | 152.8 | 299
[18 empty] | 31801411105 | [30 empty] | 14G 1.5 | 12.4 | [12 empty] | 178.3 | 344
[18 empty] | 31801811105 | [30 empty] | 18G 1.5 | 13.9 | [12 empty] | 229.2 | 437
[18 empty] | 31802511105 | [30 empty] | 25G 1.5 | 15.3 | [12 empty] | 318.3 | 612
[18 empty] | 31803411105 | [30 empty] | 34G 1.5 | 18.9 | [12 empty] | 432.9 | 820
[18 empty] | 31800201205 | [30 empty] | 2 x 2.5 | 7.5 | [12 empty] | 40.1 | 103
[18 empty] | 31800311205 | [30 empty] | 3G 2.5 | 8 | [12 empty] | 61 | 134
[18 empty] | 31800411205 | [30 empty] | 4G 2.5 | 8.9 | [12 empty] | 82 | 168
[18 empty] | 31800511205 | [30 empty] | 5G 2.5 | 9.8 | [12 empty] | 102 | 210
[18 empty] | 31800711205 | [30 empty] | 7G 2.5 | 10.7 | [12 empty] | 142 | 271
[18 empty] | 31801211205 | [30 empty] | 12G 2.5 | 14.4 | [12 empty] | 248 | 469
[18 empty] | 31800410004 | [30 empty] | 4G 4 | 10.1 | [12 empty] | 128 | 250
[18 empty] | 31800510004 | [30 empty] | 5G 4 | 11.2 | [12 empty] | 159.5 | 312
[18 empty] | 31800710004 | [30 empty] | 7G 4 | 12.3 | [12 empty] | 223.5 | 405
[18 empty] | 31800410006 | [30 empty] | 4G 6 | 12.2 | [12 empty] | 191.5 | 367
[18 empty] | 31800510006 | [30 empty] | 5G 6 | 13.5 | [12 empty] | 239.5 | 458
[18 empty] | 31800710006 | [30 empty] | 7G 6 | 14.8 | [12 empty] | 335 | 596
[18 empty] | 31800410010 | [30 empty] | 4G 10 | 14.5 | [12 empty] | 326 | 570
[18 empty] | 31800510010 | [30 empty] | 5G 10 | 16 | [12 empty] | 407.5 | 703
[18 empty] | 31800410016 | [30 empty] | 4G 16 | 17.8 | [12 empty] | 543 | 896
[18 empty] | 31800510016 | [30 empty] | 5G 16 | 19.7 | [12 empty] | 678.5 | 1119
[18 empty] | 31800410025 | [30 empty] | 4G 25 | 21.9 | [12 empty] | 844.5 | 1391
[18 empty] | 31800510025 | [30 empty] | 5G 25 | 25.8 | [12 empty] | 1055.5 | 1717
[18 empty] | 31800410035 | [30 empty] | 4G 35 | 26.4 | [12 empty] | 1189 | 1872
https://www.rrkabel.com/control-cable/control-cable-jz-hch | JZ-HCH | ['https://www.rrkabel.com/Uploads/Products/45/ProductZoomForMoreDetailsImage/Control-Cables_JZ-HCH.jpg', 'https://www.rrkabel.com/Uploads/Products/45/ProductZoomImage/Control-Cables_JZ-HCH1.jpg', 'https://www.rrkabel.com/Uploads/Products/133/ProductFeaturesDetails/sheath-25.png', 'https://www.rrkabel.com/Uploads/Products/133/ProductFeaturesDetails/sheath-25.png'] | [22 empty] | ['Halogen-free cables for airports railway station, plant engineering and Industrial machinery, in EMC sensitive instruments. Tinnedcopper braid screen ensures disturbance free transmission of data and signals.'] | [5 empty] | ['Adapted to EN 50525-3-11.'] | ['U / U 300 / 500V O'] |  | ['Flexing -15°C to +70°C. Fixed installation -30°C to +70°C'] |  |  | ['Bare copper, fine wire conductors, to EN 60228 Cl. 5.Core insulation of halogen-free compound TI6 to EN 50363-7.Black colour with white numbers DIN VDE 0293.Green/Yellow earth core in outer layer.Cores stranded in layers with optimal lay-length.Halogen free inner sheath in Grey (RAL 7001).Tinned-copper braided screen, approx. 85% coverage.Halogen-free sheath compound TM7, to EN 50363-8.Sheath colour grey (RAL 7001).'] | ['Flame retardant to IEC 60332-1-2.No flame propagation according to IEC 60332-3-24 (flame spread on Vertical cable or wire bundle).Halogen free according to IEC 60754-1.Corrosive gas evolution to IEC 60754-2.'] | [12 empty] | ['Flexing approx. 15 x cable ø. Fixed installation approx. 6 x cable ø']
[18 empty] | 31900201050 | [30 empty] | 2 x 0.5 | 7.1 | [12 empty] | 21.6 | 72
[18 empty] | 31900311050 | [30 empty] | 3G 0.5 | 7.5 | [12 empty] | 27.6 | 82
[18 empty] | 31900301050 | [30 empty] | 3 X 0.5 | 7.5 | [12 empty] | 27.6 | 82
[18 empty] | 31900411050 | [30 empty] | 4G 0.5 | 8 | [12 empty] | 32.5 | 97
[18 empty] | 31900401050 | [30 empty] | 4 X 0.5 | 8 | [12 empty] | 32.5 | 97
[18 empty] | 31900511050 | [30 empty] | 5G 0.5 | 8.5 | [12 empty] | 38.7 | 111
[18 empty] | 31900711050 | [30 empty] | 7G 0.5 | 9.1 | [12 empty] | 47.7 | 129
[18 empty] | 31901211050 | [30 empty] | 12G 0.5 | 11.3 | [12 empty] | 75.2 | 208
[18 empty] | 31900201075 | [30 empty] | 2 x 0.75 | 7.7 | [12 empty] | 27.5 | 86
[18 empty] | 31900311075 | [30 empty] | 3G 0.75 | 8.1 | [12 empty] | 36.2 | 99
[18 empty] | 31900301075 | [30 empty] | 3 X 0.75 | 8.1 | [12 empty] | 36.2 | 99
[18 empty] | 31900411075 | [30 empty] | 4G 0.75 | 8.6 | [12 empty] | 42.4 | 114
[18 empty] | 31900401075 | [30 empty] | 4 X 0.75 | 8.6 | [12 empty] | 42.4 | 114
[18 empty] | 31900511075 | [30 empty] | 5G 0.75 | 9.3 | [12 empty] | 48.7 | 130
[18 empty] | 31900501075 | [30 empty] | 5 X 0.75 | 9.3 | [12 empty] | 48.7 | 130
[18 empty] | 31900711075 | [30 empty] | 7G 0.75 | 9.9 | [12 empty] | 64 | 163
[18 empty] | 31900701075 | [30 empty] | 7 X 0.75 | 9.9 | [12 empty] | 64 | 163
[18 empty] | 31901211075 | [30 empty] | 12G 0.75 | 12.5 | [12 empty] | 101.1 | 258
[18 empty] | 31901811075 | [30 empty] | 18G 0.75 | 14.6 | [12 empty] | 160.6 | 372
[18 empty] | 31902511075 | [30 empty] | 25G 0.75 | 15.8 | [12 empty] | 214.1 | 493
[18 empty] | 31900200001 | [30 empty] | 2 x 1 | 8.1 | [12 empty] | 32 | 96
[18 empty] | 31900310001 | [30 empty] | 3G 1 | 8.4 | [12 empty] | 42.2 | 111
[18 empty] | 31900300001 | [30 empty] | 3 X 1 | 8.4 | [12 empty] | 42.2 | 111
[18 empty] | 31900410001 | [30 empty] | 4G 1 | 9.1 | [12 empty] | 50.7 | 127
[18 empty] | 31900400001 | [30 empty] | 4 X 1 | 9.1 | [12 empty] | 50.7 | 127
[18 empty] | 31900510001 | [30 empty] | 5G 1 | 9.7 | [12 empty] | 61.3 | 153
[18 empty] | 31900710001 | [30 empty] | 7G 1 | 10.4 | [12 empty] | 79.5 | 192
[18 empty] | 31901210001 | [30 empty] | 12G 1 | 13.2 | [12 empty] | 146.2 | 322
[18 empty] | 31901810001 | [30 empty] | 18G 1 | 15.4 | [12 empty] | 202.5 | 444
[18 empty] | 31902510001 | [30 empty] | 25G 1 | 16.7 | [12 empty] | 271.5 | 586
[18 empty] | 31904110001 | [30 empty] | 41G 1 | 22 | [12 empty] | 437.1 | 923
[18 empty] | 31900201105 | [30 empty] | 2 x 1.5 | 8.7 | [12 empty] | 42.1 | 116
[18 empty] | 31900311105 | [30 empty] | 3G 1.5 | 9.2 | [12 empty] | 56 | 136
[18 empty] | 31900301105 | [30 empty] | 3 X 1.5 | 9.2 | [12 empty] | 56 | 136
[18 empty] | 31900411105 | [30 empty] | 4G 1.5 | 9.6 | [12 empty] | 69.1 | 163
[18 empty] | 31900511105 | [30 empty] | 5G 1.5 | 10.6 | [12 empty] | 99.2 | 209
[18 empty] | 31900711105 | [30 empty] | 7G 1.5 | 11.3 | [12 empty] | 124.6 | 247
[18 empty] | 31901211105 | [30 empty] | 12G 1.5 | 14.8 | [12 empty] | 198.6 | 416
[18 empty] | 31901811105 | [30 empty] | 18G 1.5 | 17.2 | [12 empty] | 279.6 | 575
[18 empty] | 31902511105 | [30 empty] | 25G 1.5 | 20.1 | [12 empty] | 375.2 | 783
[18 empty] | 31900311205 | [30 empty] | 3G 2.5 | 10.4 | [12 empty] | 99.1 | 204
[18 empty] | 31900411205 | [30 empty] | 4G 2.5 | 11.4 | [12 empty] | 121.1 | 248
[18 empty] | 31900511205 | [30 empty] | 5G 2.5 | 12.6 | [12 empty] | 146.4 | 302
[18 empty] | 31900711205 | [30 empty] | 7G 1.5 | 13.9 | [12 empty] | 124.6 | 382
[18 empty] | 31901211205 | [30 empty] | 12G 2.5 | 17.6 | [12 empty] | 304.4 | 613
[18 empty] | 31900410004 | [30 empty] | 4G 4 | 13.4 | [12 empty] | 173.2 | 350
[18 empty] | 31900510004 | [30 empty] | 5G 4 | 14.7 | [12 empty] | 212.4 | 426
[18 empty] | 31900710004 | [30 empty] | 7G 4 | 16.2 | [12 empty] | 275 | 537
[18 empty] | 31900410006 | [30 empty] | 4G 6 | 15.8 | [12 empty] | 250.2 | 497
[18 empty] | 31900510006 | [30 empty] | 5G 6 | 17.3 | [12 empty] | 303.7 | 601
[18 empty] | 31900710006 | [30 empty] | 7G 6 | 18.8 | [12 empty] | 400 | 754
[18 empty] | 31900410010 | [30 empty] | 4G 10 | 19 | [12 empty] | 395.2 | 753
[18 empty] | 31900510010 | [30 empty] | 5G 10 | 21.2 | [12 empty] | 482.7 | 932
[18 empty] | 31900410016 | [30 empty] | 4G 16 | 22.2 | [12 empty] | 657.4 | 1128
[18 empty] | 31900510016 | [30 empty] | 5G 16 | 24.4 | [12 empty] | 807.2 | 1377
[18 empty] | 31900410025 | [30 empty] | 4G 25 | 27 | [12 empty] | 984.1 | 1690
[18 empty] | 31900410035 | [30 empty] | 4G 35 | 30.7 | [12 empty] | 1352 | 2257
[18 empty] | 31900410050 | [30 empty] | 4 G 50 | 36.5 | [12 empty] | 2009.2 | 3205
[18 empty] | 31900410070 | [30 empty] | 4 G 70 | 41.6 | [12 empty] | 2788.5 | 4319
[18 empty] | 31900410095 | [30 empty] | 4 G 95 | 47.8 | [12 empty] | 3656.7 | 5691
https://www.rrkabel.com/control-cable/control-cable-h05z1z1-f-318b | H05Z1Z1-F (318B) | ['https://www.rrkabel.com/Uploads/Products/180/ProductZoomForMoreDetailsImage/H05Z1Z1F318B216x252.jpg', 'https://www.rrkabel.com/Uploads/Products/180/ProductZoomImage/H05Z1Z1-F318B-with-name.jpg', 'https://www.rrkabel.com/Uploads/Products/497/ProductFeaturesDetails/H05Z1Z1_20220404.png', 'https://www.rrkabel.com/Uploads/Products/497/ProductFeaturesDetails/H05Z1Z1_20220404.png'] | [22 empty] | ['Used as an indoor general wiring cable primarily for installations in public areas or in any application where fire safety is utmost important.The cable can be used as pendant lighting drops or as a general supply lead within hospital, hotels, airport, educational institutions, etc.'] | [5 empty] | ['BS EN 50525-3-11'] | ['U', 'O', '/ U 300/500 V'] |  | ['Flexing -5°C to +70°C. Fixed Installation : -30°C to 70°C.'] |  |  |  | ['Self-extinguishing and flame retardant according to IEC 60332-1-2.', "Please complete the part numbers for these cables by adding the suffix (in place of 'z') for the sheath colour required: 1 - black (RAL 9005), 3 - grey (RAL 7001), 5 - white (RAL 9010)."] | [27 empty] | ['Bare copper, fine wire conductors, as per EN 60228 Cl.5.'] | ['LSZH (Low Smoke Zero Halogen) core insulation Type TI6, BS EN 50363-7'] | ['Harmonised core colour to HD 308 (Refer Appendix Table No. 1-1)', 'Cores stranded in layers with optimal lay-length']
[54 empty] | 03200101007z |  |  |  | 39 | 2 x 0.5 | [9 empty] | 5.25
[54 empty] | 03200102007z |  |  |  | 46 | 3 G 0.5 | [9 empty] | 5.55
[54 empty] | 03200103007z |  |  |  | 56 | 4 G 0.5 | [9 empty] | 6.05
[54 empty] | 03200104007z |  |  |  | 64 | 5 G 0.5 | [9 empty] | 6.35
[54 empty] | 03200105007z |  |  |  | 58 | 2 x 0.75 | [9 empty] | 6.45
[54 empty] | 03200106007z |  |  |  | 69 | 3 G 0.75 | [9 empty] | 6.8
[54 empty] | 03200107007z |  |  |  | 85 | 4 G 0.75 | [9 empty] | 7.4
[54 empty] | 03200108007z |  |  |  | 106 | 5 G 0.75 | [9 empty] | 8.3
[54 empty] | 03200109007z |  |  |  | 130 | 7 G 0.75 | [9 empty] | 9
[54 empty] | 03200110007z |  |  |  | 239 | 12 G 0.75 | [9 empty] | 12.35
[54 empty] | 03200111007z |  |  |  | 67 | 2 x 1 | [9 empty] | 6.75
[54 empty] | 03200112007z |  |  |  | 80 | 3 G 1 | [9 empty] | 7.15
[54 empty] | 03200113007z |  |  |  | 102 | 4 G 1 | [9 empty] | 8
[54 empty] | 03200114007z |  |  |  | 122 | 5 G 1 | [9 empty] | 8.75
[54 empty] | 03200115007z |  |  |  | 88 | 2 x 1.5 | [9 empty] | 7.65
[54 empty] | 03200116007z |  |  |  | 110 | 3 G 1.5 | [9 empty] | 8.35
[54 empty] | 03200117007z |  |  |  | 140 | 4 G 1.5 | [9 empty] | 9.3
[54 empty] | 03200118007z |  |  |  | 174 | 5 G 1.5 | [9 empty] | 10.35
[54 empty] | 03200119007z |  |  |  | 134 | 2 x 2.5 | [9 empty] | 9.3
[54 empty] | 03200120007z |  |  |  | 168 | 3 G 2.5 | [9 empty] | 10.1
[54 empty] | 03200121007z |  |  |  | 208 | 4 G 2.5 | [9 empty] | 11
[54 empty] | 03200122007z |  |  |  | 257 | 5 G 2.5 | [9 empty] | 12.25
[54 empty] | 03200123007z |  |  |  | 183 | 2 x 4 | [9 empty] | 10.25
[54 empty] | 03200124007z |  |  |  | 231 | 3 G 4 | [9 empty] | 11.42
[54 empty] | 03200125007z |  |  |  | 287 | 4 G 4 | [9 empty] | 12.49
[54 empty] | 03200126007z |  |  |  | 362 | 5 G 4 | [9 empty] | 14.05