## Sheet1
Link | Title | Images | Application | Standard | Voltage Rating | Temperature Range | Cable Type - 1 |  | Properties | Fire Performance Tests | Cable Type – 2 | Specifications | Cable Type – 3 | Technical Data | Part Number | Part Number.1 | No. of Cores & Nominal Cross Section Area (Sq. mm) | No. of Cores & Nominal Cross Section Area (Sq. mm).1 | No. of Strands / Strand Diameter (mm) | No. of Strands / Strand Diameter (mm).1 | Nominal Overall Diameter (mm) | Nominal Overall Diameter (mm).1 | ('Part Number', 'Part Number') | ('Part Number', 'Part Number.1') | ('No. of Cores & Nominal Cross Section Area (Sq. mm)', 'No. of Cores & Nominal Cross Section Area (Sq. mm)') | ('No. of Cores & Nominal Cross Section Area (Sq. mm)', 'No. of Cores & Nominal Cross Section Area (Sq. mm).1') | ('Max. Conductor Resistance at 20°C (Ω/km)', 'Max. Conductor Resistance at 20°C (Ω/km)') | ('Max. Conductor Resistance at 20°C (Ω/km)', 'Max. Conductor Resistance at 20°C (Ω/km).1') | ('Current Rating (A)', 'DC or Single Phase AC enclosed') | ('Current Rating (A)', 'DC or Single Phase AC enclosed.1') | ('Current Rating (A)', 'DC or Single Phase AC Clipped') | ('Current Rating (A)', 'DC or Single Phase AC Clipped.1') | ('Voltage Drop DC or Single Phase AC (mV/A/m)', 'Voltage Drop DC or Single Phase AC (mV/A/m)') | ('Voltage Drop DC or Single Phase AC (mV/A/m)', 'Voltage Drop DC or Single Phase AC (mV/A/m).1') | Operating Temperature | Construction | Conductor | Bedding | Unnamed: 0 | Nominal Cross Sectional Area (Sq. mm) | Nominal Cross Sectional Area (Sq. mm).1 | Insulation Thickness (mm) | Insulation Thickness (mm).1 | Nominal Armour Wire Diameter (mm) | Nominal Armour Wire Diameter (mm).1 | Approx. Diameter Under Armour (mm) | Approx. Diameter Under Armour (mm).1 | Approx. Overall Diameter (mm) | Approx. Overall Diameter (mm).1 | Approx. Cable Weight (kg/km) | Approx. Cable Weight (kg/km).1 | Max. DC Conductor Resistance at 20°C (O/km) | Max. DC Conductor Resistance at 20°C (O/km).1 | Max. AC Conductor Resistance at 90°C (O/km) | Max. AC Conductor Resistance at 90°C (O/km).1 | Reactance at 50Hz (O/km) | Reactance at 50Hz (O/km).1 | AC Impedance at 90°C (O/km) | AC Impedance at 90°C (O/km).1 | Max. Arm. Resistance at 20°C (O/km) | Max. Arm. Resistance at 20°C (O/km).1 | Voltage rating | Operating temperature | Conductors | Cable Construction | Circuit Integrity for installation in metal conduits | Acid Gas Emission | Smoke Emission | Nominal CrossSectional Area (Sq. mm) | Max. Overall Diameter (mm) | ('Conductor Cross Sectional area', 'Conductor Cross Sectional area', 'Conductor Cross Sectional area', '1', '(mm²)') | ('Reference Method A (Enclosed in Conduits in Thermally Insulating Wall, etc.)', '2 Cable, Single-Phase AC or DC', '2 Cable, Single-Phase AC or DC', '2', '(A)') | ('Reference Method A (Enclosed in Conduits in Thermally Insulating Wall, etc.)', '3 or 4 Cables,Three-Phase AC', '3 or 4 Cables,Three-Phase AC', '3', '(A)') | ('Reference Method B (Enclosed in Conduits on a Wall or in Trunking, etc.)', '2 Cable, Single-Phase AC or DC', '2 Cable, Single-Phase AC or DC', '4', '(A)') | ('Reference Method B (Enclosed in Conduits on a Wall or in Trunking, etc.)', '3 or 4 Cables,Three-Phase AC', '3 or 4 Cables,Three-Phase AC', '5', '(A)') | ('Reference Method C (Clipped Direct)', '2 Cable, Single-Phase AC or DC Flat andTouching', '2 Cable, Single-Phase AC or DC Flat andTouching', '6', '(A)') | ('Reference Method C (Clipped Direct)', '3 or 4 Cables, Three-Phase AC Flat andTouching orTrefoil', '3 or 4 Cables, Three-Phase AC Flat andTouching orTrefoil', '7', '(A)') | ('Reference Method F (in Free Air or on Perforated Cable Tray etc. Horizontal or Vertical etc.) Touching', '2 Cable, Single-Phase AC or DC Flat', '2 Cable, Single-Phase AC or DC Flat', '8', '(A)') | ('Reference Method F (in Free Air or on Perforated Cable Tray etc. Horizontal or Vertical etc.) Touching', '3 Cables, Three-Phase AC Flat', '3 Cables, Three-Phase AC Flat', '9', '(A)') | ('Reference Method F (in Free Air or on Perforated Cable Tray etc. Horizontal or Vertical etc.) Touching', '3 Cables, Three-Phase AC Trefoil', '3 Cables, Three-Phase AC Trefoil', '10', '(A)') | ('Reference Method G (in free air) Spaced byOne Cable Diameter', '2 Cable, Single-Phase AC or DC or 3 Cables. Three-Phase AC Flat', 'Horizontol', '11', '(A)') | ('Reference Method G (in free air) Spaced byOne Cable Diameter', '2 Cable, Single-Phase AC or DC or 3 Cables. Three-Phase AC Flat', 'Vertical', '12', '(A)') | ('2 Cable DC', '2 Cable DC', '2 Cable DC', '2', '(mV/A/m)') | ('2 Cables, Single-Phase AC', 'Reference MethodA & B (Enclosedin Conduit orTrunking )', 'Reference MethodA & B (Enclosedin Conduit orTrunking )', '3', '(mV/A/m)') | ('2 Cables, Single-Phase AC', 'Reference MethodA & B (Enclosedin Conduit orTrunking )', 'Reference MethodA & B (Enclosedin Conduit orTrunking )', '3', '(mV/A/m).1') | ('2 Cables, Single-Phase AC', 'Reference MethodA & B (Enclosedin Conduit orTrunking )', 'Reference MethodA & B (Enclosedin Conduit orTrunking )', '3', '(mV/A/m).2') | ('2 Cables, Single-Phase AC', 'Reference Methods C, F & G (Clipped Direct, on Tray or in Free Air)', 'Cable Touching', '4', '(mV/A/m)') | ('2 Cables, Single-Phase AC', 'Reference Methods C, F & G (Clipped Direct, on Tray or in Free Air)', 'Cable Touching', '4', '(mV/A/m).1') | ('2 Cables, Single-Phase AC', 'Reference Methods C, F & G (Clipped Direct, on Tray or in Free Air)', 'Cable Touching', '4', '(mV/A/m).2') | ('2 Cables, Single-Phase AC', 'Reference Methods C, F & G (Clipped Direct, on Tray or in Free Air)', 'Cable Spaced', '5', '(mV/A/m)') | ('2 Cables, Single-Phase AC', 'Reference Methods C, F & G (Clipped Direct, on Tray or in Free Air)', 'Cable Spaced', '5', '(mV/A/m).1') | ('2 Cables, Single-Phase AC', 'Reference Methods C, F & G (Clipped Direct, on Tray or in Free Air)', 'Cable Spaced', '5', '(mV/A/m).2') | ('3 or 4 Cables, Three-Phase AC', 'Reference Method A & B (Enclosed in Conduit or Trunking)', 'Reference Method A & B (Enclosed in Conduit or Trunking)', '6', '(mV/A/m)') | ('3 or 4 Cables, Three-Phase AC', 'Reference Method A & B (Enclosed in Conduit or Trunking)', 'Reference Method A & B (Enclosed in Conduit or Trunking)', '6', '(mV/A/m).1') | ('3 or 4 Cables, Three-Phase AC', 'Reference Method A & B (Enclosed in Conduit or Trunking)', 'Reference Method A & B (Enclosed in Conduit or Trunking)', '6', '(mV/A/m).2') | ('3 or 4 Cables, Three-Phase AC', 'Reference Method C, F & G (Clipped Direct, on Tray or in Free Air)', 'Cables Touching,Tre foil', '7', '(mV/A/m)') | ('3 or 4 Cables, Three-Phase AC', 'Reference Method C, F & G (Clipped Direct, on Tray or in Free Air)', 'Cables Touching,Tre foil', '7', '(mV/A/m).1') | ('3 or 4 Cables, Three-Phase AC', 'Reference Method C, F & G (Clipped Direct, on Tray or in Free Air)', 'Cables Touching,Tre foil', '7', '(mV/A/m).2') | ('3 or 4 Cables, Three-Phase AC', 'Reference Method C, F & G (Clipped Direct, on Tray or in Free Air)', 'Cables Touching, Flat', '8', '(mV/A/m)') | ('3 or 4 Cables, Three-Phase AC', 'Reference Method C, F & G (Clipped Direct, on Tray or in Free Air)', 'Cables Touching, Flat', '8', '(mV/A/m).1') | ('3 or 4 Cables, Three-Phase AC', 'Reference Method C, F & G (Clipped Direct, on Tray or in Free Air)', 'Cables Touching, Flat', '8', '(mV/A/m).2') | ('3 or 4 Cables, Three-Phase AC', 'Reference Method C, F & G (Clipped Direct, on Tray or in Free Air)', 'Cables Spaced*, Flat', '9', '(mV/A/m)') | ('3 or 4 Cables, Three-Phase AC', 'Reference Method C, F & G (Clipped Direct, on Tray or in Free Air)', 'Cables Spaced*, Flat', '9', '(mV/A/m).1') | ('3 or 4 Cables, Three-Phase AC', 'Reference Method C, F & G (Clipped Direct, on Tray or in Free Air)', 'Cables Spaced*, Flat', '9', '(mV/A/m).2') | ('Unnamed: 23_level_0', 'Unnamed: 23_level_1', 'Unnamed: 23_level_2', 'Unnamed: 23_level_3', 'Unnamed: 23_level_4')
https://www.rrkabel.com/fire-security-cable/fire-alarm-cables | FIRE ALARM CABLES | ['https://www.rrkabel.com/Uploads/Products/99/ProductZoomForMoreDetailsImage/Fire-Alarm-Cable.jpg', 'https://www.rrkabel.com/Uploads/Products/99/ProductZoomImage/03.jpg', 'https://www.rrkabel.com/Uploads/Products/295/ProductFeaturesDetails/01.png', 'https://www.rrkabel.com/Uploads/Products/295/ProductFeaturesDetails/01.png'] | ['These cables are used in high rise buildings, commercial complexes, schools and educational institutions, hospitals, etc. for the connection with security systems like smoke detectors, emergency lightings, exit signboards and fire command center. These cables are used where the fire safety is utmost important.'] | ['BS 7629-1, BS EN 50200.'] | ['300/500V'] | ['-30°C to + 70°C (The cable should not be flexed when either the ambient or cable temperature is below 0°C)'] | ['FFX200 05mSOZ1-R - CU/MGT/SR/OSCR/LSZH 300/500V Class 2.'] | ['Plain annealed copper conductor to BS EN 60228, class 2.', 'Primary insulation of glass mica fire resistant tape.', 'Secondary insulation of high performance silicone rubber.', 'E I 2 to BS 7655 Section 1.1.'] | ['*Low smoke zero halogen (LSOH), flame retardant.'] | ['BS 7629 -1, 300 / 500V fire resistant electric cables with non corrosive gases and low emission of smoke when affected by fire. Category STANDARD 60 when tested in accordance with BS EN 50200-Method of test for resistance to fire of unprotected small cables for use in emergency circuits. In addition, it shall meet the 30 min survival time when tested in accordance with BS EN 502000,Annex E. Meets requirement for the fire resistant cables as described in clause 262d of BS 5839-1'] | ['FFX200 05SOZ1-U – CU/SR/OSCR/LSZH 300/500V Class 1.'] | ['Plain annealed copper conductor Cl.1, to BS EN 60288. Insulation of high performance Silicone rubber. EI 2 to BS 7655 Section 1.1. Core colours: 2 Core : blue, brown. 3 Core : blue, brown, black. 4 Core : blue, brown, black, grey. Earth/Drain wire of annealed tinned copper Cl.1 to BS EN 60228. Electrostatic screen of aluminium fire barrier with 125 % overlap. Sheath Type LTS3 to BS 7655 section 6.1.'] | ['FFX200 05mZOZ1-R – CU/MGT/LS0H/OSCR/LS0H 300/500V Class 2.'] | ['Plain annealed copper conductor to BS EN 60288, class 2. Primary insulation of glass mica fire resistant tape. Secondary insulation to BS EN 50363-5, Type EI 5, Low smoke zero halogen (LSZH) cross-linkable flame retardant insulation.', 'Core colours: 2 Core : blue, brown. 3 Core : blue, brown, black. 4 Core : blue, brown, black, grey. Glass fibre tape. Earth/Drain wire of annealed tinned copper to BS EN 60228. Electrostatic screen of aluminium fire barrier. Sheath Type LTS3 to BS 7655 section 6.1.']
[15 empty] | 100100201105 | 100100201105 | 2 x 1.5 | 2 x 1.5 | 7/0.53 | 7/0.53 | 10 | 10
[15 empty] | 100100201205 | 100100201205 | 2 x 2.5 | 2 x 2.5 | 7/0.67 | 7/0.67 | 11.5 | 11.5
[15 empty] | 100100301105 | 100100301105 | 3 x 1.5 | 3 x 1.5 | 7/0.53 | 7/0.53 | 10.8 | 10.8
[15 empty] | 100100301205 | 100100301205 | 3 x 2.5 | 3 x 2.5 | 7/0.67 | 7/0.67 | 12.5 | 12.5
[15 empty] | 100100401105 | 100100401105 | 4 x 1.5 | 4 x 1.5 | 7/0.53 | 7/0.53 | 12 | 12
[15 empty] | 100100401205 | 100100401205 | 4 x 2.5 | 4 x 2.5 | 7/0.67 | 7/0.67 | 13.5 | 13.5
[23 empty] | 100100201105 | 100100201105 | 2 x 1.5 | 2 x 1.5 | 12.1 | 12.1 | 17.5 | 17.5 | 20 | 20 | 29 | 29
[23 empty] | 100100201205 | 100100201205 | 2 x 2.5 | 2 x 2.5 | 7.41 | 7.41 | 24 | 24 | 27 | 27 | 18 | 18
[23 empty] | 100100301105 | 100100301105 | 3 x 1.5 | 3 x 1.5 | 12.1 | 12.1 | 17.5 | 17.5 | 20 | 20 | 29 | 29
[23 empty] | 100100301205 | 100100301205 | 3 x 2.5 | 3 x 2.5 | 7.41 | 7.41 | 24 | 24 | 27 | 27 | 18 | 18
[23 empty] | 100100401105 | 100100401105 | 4 x 1.5 | 4 x 1.5 | 12.1 | 12.1 | 17.5 | 17.5 | 20 | 20 | 29 | 29
[23 empty] | 100100401205 | 100100401205 | 4 x 2.5 | 4 x 2.5 | 7.41 | 7.41 | 24 | 24 | 27 | 27 | 18 | 18
[15 empty] | 100200200001 | 100200200001 | 2 x 1 | 2 x 1 | 1/1.13 | 1/1.13 | 7.5 | 7.5
[15 empty] | 100200201105 | 100200201105 | 2 x 1.5 | 2 x 1.5 | 1/1.38 | 1/1.38 | 8.5 | 8.5
[15 empty] | 100200201205 | 100200201205 | 2 x 2.5 | 2 x 2.5 | 1/1.78 | 1/1.78 | 9.9 | 9.9
[15 empty] | 100200301105 | 100200301105 | 3 x 1.5 | 3 x 1.5 | 1/1.38 | 1/1.38 | 9.1 | 9.1
[15 empty] | 100200301205 | 100200301205 | 3 x 2.5 | 3 x 2.5 | 1/1.78 | 1/1.78 | 10.7 | 10.7
[15 empty] | 100200401105 | 100200401105 | 4 x 1.5 | 4 x 1.5 | 1/1.38 | 1/1.38 | 10.1 | 10.1
[15 empty] | 100200401205 | 100200401205 | 4 x 2.5 | 4 x 2.5 | 1/1.78 | 1/1.78 | 11.6 | 11.6
[23 empty] | 100200200001 | 100200200001 | 2 x 1 | 2 x 1 | 18.1 | 18.1 | 13.1 | 13.1 | 15.5 | 15.5 | 44 | 44
[23 empty] | 100200201105 | 100200201105 | 2 x 1.5 | 2 x 1.5 | 12.1 | 12.1 | 17.5 | 17.5 | 20 | 20 | 29 | 29
[23 empty] | 100200201205 | 100200201205 | 2 x 2.5 | 2 x 2.5 | 7.41 | 7.41 | 24 | 24 | 27 | 27 | 18 | 18
[23 empty] | 100200301105 | 100200301105 | 3 x 1.5 | 3 x 1.5 | 12.1 | 12.1 | 17.5 | 17.5 | 20 | 20 | 29 | 29
[23 empty] | 100200301205 | 100200301205 | 3 x 2.5 | 3 x 2.5 | 7.41 | 7.41 | 24 | 24 | 27 | 27 | 18 | 18
[23 empty] | 100200401105 | 100200401105 | 4 x 1.5 | 4 x 1.5 | 12.1 | 12.1 | 17.5 | 17.5 | 20 | 20 | 29 | 29
[23 empty] | 100200401205 | 100200401205 | 4 x 2.5 | 4 x 2.5 | 7.41 | 7.41 | 24 | 24 | 27 | 27 | 18 | 18
[15 empty] | 100300201105 | 100300201105 | 2 x 1.5 | 2 x 1.5 | 7/0.53 | 7/0.53 | 10 | 10
[15 empty] | 100300201205 | 100300201205 | 2 x 2.5 | 2 x 2.5 | 7/0.67 | 7/0.67 | 11.5 | 11.5
[15 empty] | 100300301105 | 100300301105 | 3 x 1.5 | 3 x 1.5 | 7/0.53 | 7/0.53 | 10.8 | 10.8
[15 empty] | 100300301205 | 100300301205 | 3 x 2.5 | 3 x 2.5 | 7/0.67 | 7/0.67 | 12.3 | 12.3
[15 empty] | 100200401105 | 100200401105 | 4 x 1.5 | 4 x 1.5 | 7/0.53 | 7/0.53 | 12 | 12
[15 empty] | 100200401205 | 100200401205 | 4 x 2.5 | 4 x 2.5 | 7/0.67 | 7/0.67 | 13.5 | 13.5
[23 empty] | 100300201105 | 100300201105 | 2 x 1.5 | 2 x 1.5 | 12.1 | 12.1 | 17.5 | 17.5 | 20 | 20 | 29 | 29
[23 empty] | 100300201205 | 100300201205 | 2 x 2.5 | 2 x 2.5 | 7.41 | 7.41 | 24 | 24 | 27 | 27 | 18 | 18
[23 empty] | 100300301105 | 100300301105 | 3 x 1.5 | 3 x 1.5 | 12.1 | 12.1 | 17.5 | 17.5 | 20 | 20 | 29 | 29
[23 empty] | 100300301205 | 100300301205 | 3 x 2.5 | 3 x 2.5 | 7.41 | 7.41 | 24 | 24 | 27 | 27 | 18 | 18
[23 empty] | 100300401105 | 100300401105 | 4 x 1.5 | 4 x 1.5 | 12.1 | 12.1 | 17.5 | 17.5 | 20 | 20 | 29 | 29
[23 empty] | 100300401205 | 100300401205 | 4 x 2.5 | 4 x 2.5 | 7.41 | 7.41 | 24 | 24 | 27 | 27 | 18 | 18
https://www.rrkabel.com/fire-security-cable/fire-survival-cable | FIRE SURVIVAL CABLE | ['https://www.rrkabel.com/Uploads/Products/100/ProductZoomForMoreDetailsImage/Fire-Survival-Cables.jpg', 'https://www.rrkabel.com/Uploads/Products/100/ProductZoomImage/03.jpg', 'https://www.rrkabel.com/Uploads/Products/298/ProductFeaturesDetails/01.png', 'https://www.rrkabel.com/Uploads/Products/298/ProductFeaturesDetails/01.png'] | ['These cables offer the advantages of an armoured 600/1000V rated, low smoke zero halogen (LSZH) cable with circuit integrity. They are intended for use in installations where vital circuits are required to continue operation in the event of the outbreak of fire. It is particularly suited for use in public buildings and constructions (such as hospitals, theatres, shopping developments, tunnels, mass transit railways, oil & petrochemical plants, power stations and computer installations) where the danger to life, equipment and structures may be greatly increased in the event of a power failure due to fire.'] | ['BS 7846'] | ['600 / 1000V'] | [29 empty] | ['-40°C to + 90°C', '(The cable should not be flexed when either the ambient or cable temperature is below 0°C)'] | ['Plain annealed stranded copper conductors.'] | ['For sizes up to and including 16mm² are offered in circular . Shaped conductors are offered from 25 mm² and onwards. Insulation : Mica (fire - resistant) tapes, covered by an extruded layer of cross - linked polyethylene.'] | ['An extruded layer of thermoplastic low smoke zero halogen (LSZH) compound. Armour : Single layer of galvanized steel wires.']
[15 empty] | 100300201105 | 100300201105 | [22 empty] | 2 Core | 1.5* | 1.5* | 0.6 | 0.6 | 0.9 | 0.9 | 8.5 | 8.5 | 13 | 13 | 415 | 415 | 12.1 | 12.1 | 15.428 | 15.428 | 0.104 | 0.104 | 15.428 | 15.428 | 10.7 | 10.7
[15 empty] | 100300201105 | 100300201105 | [22 empty] | 2 Core | 1.5* | 1.5* | 0.6 | 0.6 | 0.9 | 0.9 | 8.5 | 8.5 | 13 | 13 | 415 | 415 | 12.1 | 12.1 | 15.428 | 15.428 | 0.104 | 0.104 | 15.428 | 15.428 | 10.7 | 10.7
[15 empty] | 100300201205 | 100300201205 | [22 empty] | 2 Core | 2.5* | 2.5* | 0.7 | 0.7 | 0.9 | 0.9 | 10 | 10 | 14.5 | 14.5 | 495 | 495 | 7.41 | 7.41 | 9.448 | 9.448 | 0.101 | 0.101 | 9.448 | 9.448 | 8.8 | 8.8
[15 empty] | 100300200004 | 100300200004 | [22 empty] | 2 Core | 4* | 4* | 0.7 | 0.7 | 0.9 | 0.9 | 11 | 11 | 15.5 | 15.5 | 575 | 575 | 4.61 | 4.61 | 5.878 | 5.878 | 0.099 | 0.099 | 5.878 | 5.878 | 7.9 | 7.9
[15 empty] | 100300200006 | 100300200006 | [22 empty] | 2 Core | 6* | 6* | 0.7 | 0.7 | 0.9 | 0.9 | 12.5 | 12.5 | 17 | 17 | 658 | 658 | 3.08 | 3.08 | 3.927 | 3.927 | 0.094 | 0.094 | 3.928 | 3.928 | 7 | 7
[15 empty] | 100300200010 | 100300200010 | [22 empty] | 2 Core | 10* | 10* | 0.7 | 0.7 | 0.9 | 0.9 | 14 | 14 | 19 | 19 | 828 | 828 | 1.83 | 1.83 | 2.333 | 2.333 | 0.093 | 0.093 | 2.335 | 2.335 | 6 | 6
[15 empty] | 100300200016 | 100300200016 | [22 empty] | 2 Core | 16 | 16 | 0.7 | 0.7 | 1.25 | 1.25 | 16 | 16 | 21.5 | 21.5 | 1005 | 1005 | 1.15 | 1.15 | 1.466 | 1.466 | 0.088 | 0.088 | 1.469 | 1.469 | 3.8 | 3.8
[15 empty] | 100300200025 | 100300200025 | [22 empty] | 2 Core | 25 | 25 | 0.9 | 0.9 | 1.25 | 1.25 | 15.5 | 15.5 | 21.2 | 21.2 | 1105 | 1105 | 0.727 | 0.727 | 0.927 | 0.927 | 0.082 | 0.082 | 0.93 | 0.93 | 3.7 | 3.7
[15 empty] | 100300200035 | 100300200035 | [22 empty] | 2 Core | 35 | 35 | 0.9 | 0.9 | 1.6 | 1.6 | 17.5 | 17.5 | 24 | 24 | 1555 | 1555 | 0.524 | 0.524 | 0.668 | 0.668 | 0.077 | 0.077 | 0.673 | 0.673 | 2.5 | 2.5
[15 empty] | 100300200050 | 100300200050 | [22 empty] | 2 Core | 50 | 50 | 1 | 1 | 1.6 | 1.6 | 20 | 20 | 26.5 | 26.5 | 1855 | 1855 | 0.387 | 0.387 | 0.494 | 0.494 | 0.076 | 0.076 | 0.5 | 0.5 | 2.3 | 2.3
[15 empty] | 100300200070 | 100300200070 | [22 empty] | 2 Core | 70 | 70 | 1.1 | 1.1 | 1.6 | 1.6 | 23 | 23 | 30 | 30 | 2455 | 2455 | 0.268 | 0.268 | 0.342 | 0.342 | 0.075 | 0.075 | 0.349 | 0.349 | 2 | 2
[15 empty] | 100300200095 | 100300200095 | [22 empty] | 2 Core | 95 | 95 | 1.1 | 1.1 | 2 | 2 | 26 | 26 | 34 | 34 | 3345 | 3345 | 0.193 | 0.193 | 0.247 | 0.247 | 0.074 | 0.074 | 0.258 | 0.258 | 1.4 | 1.4
[15 empty] | 100300200120 | 100300200120 | [22 empty] | 2 Core | 120 | 120 | 1.2 | 1.2 | 2 | 2 | 29 | 29 | 37 | 37 | 3898 | 3898 | 0.153 | 0.153 | 0.196 | 0.196 | 0.072 | 0.072 | 0.209 | 0.209 | 1.3 | 1.3
[15 empty] | 100300200150 | 100300200150 | [22 empty] | 2 Core | 150 | 150 | 1.4 | 1.4 | 2 | 2 | 32 | 32 | 40 | 40 | 4645 | 4645 | 0.124 | 0.124 | 0.16 | 0.16 | 0.073 | 0.073 | 0.176 | 0.176 | 1.2 | 1.2
[15 empty] | 100300200185 | 100300200185 | [22 empty] | 2 Core | 185 | 185 | 1.6 | 1.6 | 2.5 | 2.5 | 36 | 36 | 45.5 | 45.5 | 5945 | 5945 | 0.0991 | 0.0991 | 0.128 | 0.128 | 0.073 | 0.073 | 0.148 | 0.148 | 0.82 | 0.82
[15 empty] | 100300200240 | 100300200240 | [22 empty] | 2 Core | 240 | 240 | 1.7 | 1.7 | 2.5 | 2.5 | 40 | 40 | 50 | 50 | 7345 | 7345 | 0.0754 | 0.0754 | 0.099 | 0.099 | 0.072 | 0.072 | 0.122 | 0.122 | 0.73 | 0.73
[15 empty] | 100300200300 | 100300200300 | [22 empty] | 2 Core | 300 | 300 | 1.8 | 1.8 | 2.5 | 2.5 | 44 | 44 | 54.5 | 54.5 | 8695 | 8695 | 0.0601 | 0.0601 | 0.08 | 0.08 | 0.072 | 0.072 | 0.107 | 0.107 | 0.67 | 0.67
[15 empty] | 100300200400 | 100300200400 | [22 empty] | 2 Core | 400 | 400 | 2 | 2 | 2.5 | 2.5 | 49.5 | 49.5 | 60 | 60 | 10745 | 10745 | 0.047 | 0.047 | 0.064 | 0.064 | 0.071 | 0.071 | 0.096 | 0.096 | 0.59 | 0.59
[15 empty] | 100300301105 | 100300301105 | [22 empty] | 3 Core | 1.5* | 1.5* | 0.6 | 0.6 | 0.9 | 0.9 | 9 | 9 | 13.5 | 13.5 | 423 | 423 | 12.1 | 12.1 | 15.428 | 15.428 | 0.104 | 0.104 | 15.428 | 15.428 | 10.2 | 10.2
[15 empty] | 100300301105 | 100300301105 | [22 empty] | 3 Core | 1.5* | 1.5* | 0.6 | 0.6 | 0.9 | 0.9 | 9 | 9 | 13.5 | 13.5 | 423 | 423 | 12.1 | 12.1 | 15.428 | 15.428 | 0.104 | 0.104 | 15.428 | 15.428 | 10.2 | 10.2
[15 empty] | 100300301205 | 100300301205 | [22 empty] | 3 Core | 2.5* | 2.5* | 0.7 | 0.7 | 0.9 | 0.9 | 10.5 | 10.5 | 15 | 15 | 544 | 544 | 741 | 741 | 9.448 | 9.448 | 0.101 | 0.101 | 9.448 | 9.448 | 8.2 | 8.2
[15 empty] | 100300300004 | 100300300004 | [22 empty] | 3 Core | 4* | 4* | 0.7 | 0.7 | 0.9 | 0.9 | 11.5 | 11.5 | 16.5 | 16.5 | 644 | 644 | 4.61 | 4.61 | 5.878 | 5.878 | 0.099 | 0.099 | 5.878 | 5.878 | 7.5 | 7.5
[15 empty] | 100300300006 | 100300300006 | [22 empty] | 3 Core | 6* | 6* | 0.7 | 0.7 | 0.9 | 0.9 | 13 | 13 | 17.5 | 17.5 | 738 | 738 | 3.08 | 3.08 | 3.927 | 3.927 | 0.094 | 0.094 | 3.925 | 3.925 | 6.6 | 6.6
[15 empty] | 100300300010 | 100300300010 | [22 empty] | 3 Core | 10″ | 10″ | 0.7 | 0.7 | 1.25 | 1.25 | 15 | 15 | 20.5 | 20.5 | 1085 | 1085 | 1.83 | 1.83 | 2.333 | 2.333 | 0.093 | 0.093 | 2.335 | 2.335 | 4 | 4
[15 empty] | 100300300016 | 100300300016 | [22 empty] | 3 Core | 16 | 16 | 0.7 | 0.7 | 1.25 | 1.25 | 17 | 17 | 22.5 | 22.5 | 1313 | 1313 | 1.15 | 1.15 | 1.466 | 1.466 | 0.088 | 0.088 | 1.469 | 1.469 | 3.6 | 3.6
[15 empty] | 100300300025 | 100300300025 | [22 empty] | 3 Core | 25 | 25 | 0.9 | 0.9 | 1.6 | 1.6 | 20 | 20 | 26.5 | 26.5 | 1803 | 1803 | 0.727 | 0.727 | 0.927 | 0.927 | 0.082 | 0.082 | 0.93 | 0.93 | 2.5 | 2.5
[15 empty] | 100300300035 | 100300300035 | [22 empty] | 3 Core | 35 | 35 | 0.9 | 0.9 | 1.6 | 1.6 | 22 | 22 | 29 | 29 | 2202 | 2202 | 0.524 | 0.524 | 0.668 | 0.668 | 0.077 | 0.077 | 0.673 | 0.673 | 2.3 | 2.3
[15 empty] | 100300300050 | 100300300050 | [22 empty] | 3 Core | 50 | 50 | 1 | 1 | 1.6 | 1.6 | 22.5 | 22.5 | 29.5 | 29.5 | 2453 | 2453 | 0.387 | 0.387 | 0.494 | 0.494 | 0.076 | 0.076 | 0.5 | 0.5 | 2 | 2
[15 empty] | 100300300070 | 100300300070 | [22 empty] | 3 Core | 70 | 70 | 1.1 | 1.1 | 1.6 | 1.6 | 26 | 26 | 33 | 33 | 3202 | 3202 | 0.268 | 0.268 | 0.342 | 0.342 | 0.075 | 0.075 | 0.349 | 0.349 | 1.8 | 1.8
[15 empty] | 100300300095 | 100300300095 | [22 empty] | 3 Core | 95 | 95 | 1.1 | 1.1 | 2 | 2 | 30 | 30 | 38 | 38 | 4455 | 4455 | 0.193 | 0.193 | 0.247 | 0.247 | 0.074 | 0.074 | 0.258 | 0.258 | 1.3 | 1.3
[15 empty] | 100300300120 | 100300300120 | [22 empty] | 3 Core | 120 | 120 | 1.2 | 1.2 | 2 | 2 | 33 | 33 | 41.5 | 41.5 | 5305 | 5305 | 0.153 | 0.153 | 0.196 | 0.196 | 0.072 | 0.072 | 0.209 | 0.209 | 1.2 | 1.2
[15 empty] | 100300300150 | 100300300150 | [22 empty] | 3 Core | 150 | 150 | 1.4 | 1.4 | 2.5 | 2.5 | 37 | 37 | 46.5 | 46.5 | 6705 | 6705 | 0.124 | 0.124 | 0.16 | 0.16 | 0.073 | 0.073 | 0.176 | 0.176 | 0.78 | 0.78
[15 empty] | 100300300185 | 100300300185 | [22 empty] | 3 Core | 185 | 185 | 1.6 | 1.6 | 2.5 | 2.5 | 41 | 41 | 51 | 51 | 8052 | 8052 | 0.0991 | 0.0991 | 0.128 | 0.128 | 0.073 | 0.073 | 0.148 | 0.148 | 0.71 | 0.71
[15 empty] | 100300300240 | 100300300240 | [22 empty] | 3 Core | 240 | 240 | 1.7 | 1.7 | 2.5 | 2.5 | 46 | 46 | 56 | 56 | 9953 | 9953 | 0.0754 | 0.0754 | 0.099 | 0.099 | 0.072 | 0.072 | 0.122 | 0.122 | 0.63 | 0.63
[15 empty] | 100300300300 | 100300300300 | [22 empty] | 3 Core | 300 | 300 | 1.8 | 1.8 | 2.5 | 2.5 | 51 | 51 | 61 | 61 | 12053 | 12053 | 0.0601 | 0.0601 | 0.08 | 0.08 | 0.072 | 0.072 | 0.107 | 0.107 | 0.58 | 0.58
[15 empty] | 100300300400 | 100300300400 | [22 empty] | 3 Core | 400 | 400 | 2 | 2 | 2.5 | 2.5 | 57 | 57 | 67.5 | 67.5 | 14803 | 14803 | 0.047 | 0.047 | 0.064 | 0.064 | 0.071 | 0.071 | 0.096 | 0.096 | 0.52 | 0.52
[15 empty] | 100300301105 | 100300301105 | [22 empty] | 4 Core | 1.5* | 1.5* | 0.6 | 0.6 | 0.9 | 0.9 | 9 | 9 | 13.5 | 13.5 | 423 | 423 | 12.1 | 12.1 | 15.428 | 15.428 | 0.104 | 0.104 | 15.428 | 15.428 | 10.2 | 10.2
[15 empty] | 100300401105 | 100300401105 | [22 empty] | 4 Core | 1.5* | 1.5* | 0.6 | 0.6 | 0.9 | 0.9 | 10 | 10 | 14.8 | 14.8 | 522 | 522 | 12.1 | 12.1 | 15.428 | 15.428 | 0.104 | 0.104 | 15.428 | 15.428 | 9.5 | 9.5
[15 empty] | 100300401205 | 100300401205 | [22 empty] | 4 Core | 2.5* | 2.5* | 0.7 | 0.7 | 0.9 | 0.9 | 11.5 | 11.5 | 16 | 16 | 618 | 618 | 7.41 | 7.41 | 9.448 | 9.448 | 0.101 | 0.101 | 9.448 | 9.448 | 7.7 | 7.7
[15 empty] | 100300400004 | 100300400004 | [22 empty] | 4 Core | 4* | 4* | 0.7 | 0.7 | 0.9 | 0.9 | 13 | 13 | 17.8 | 17.8 | 725 | 725 | 4.61 | 4.61 | 5.878 | 5.878 | 0.099 | 0.099 | 5.878 | 5.878 | 6.8 | 6.8
[15 empty] | 100300400006 | 100300400006 | [22 empty] | 4 Core | 6* | 6* | 0.7 | 0.7 | 1.25 | 1.25 | 14.5 | 14.5 | 20 | 20 | 985 | 985 | 3.08 | 3.08 | 3.927 | 3.927 | 0.094 | 0.094 | 3.925 | 3.925 | 4.3 | 4.3
[15 empty] | 100300400010 | 100300400010 | [22 empty] | 4 Core | 10* | 10* | 0.7 | 0.7 | 1.25 | 1.25 | 16.5 | 16.5 | 22 | 22 | 1255 | 1255 | 1.83 | 1.83 | 2.333 | 2.333 | 0.093 | 0.093 | 2.335 | 2.335 | 3.7 | 3.7
[15 empty] | 100300400016 | 100300400016 | [22 empty] | 4 Core | 16 | 16 | 0.7 | 0.7 | 1.25 | 1.25 | 19 | 19 | 24.5 | 24.5 | 1635 | 1635 | 1.15 | 1.15 | 1.466 | 1.466 | 0.088 | 0.088 | 1.469 | 1.469 | 3.2 | 3.2
[15 empty] | 100300400025 | 100300400025 | [22 empty] | 4 Core | 25 | 25 | 0.9 | 0.9 | 1.6 | 1.6 | 22 | 22 | 28.5 | 28.5 | 2145 | 2145 | 0.727 | 0.727 | 0.927 | 0.927 | 0.082 | 0.082 | 0.93 | 0.93 | 2.3 | 2.3
[15 empty] | 100300400035 | 100300400035 | [22 empty] | 4 Core | 35 | 35 | 0.9 | 0.9 | 1.6 | 1.6 | 24.5 | 24.5 | 31.5 | 31.5 | 2645 | 2645 | 0.524 | 0.524 | 0.668 | 0.668 | 0.077 | 0.077 | 0.673 | 0.673 | 2 | 2
[15 empty] | 100300400050 | 100300400050 | [22 empty] | 4 Core | 50 | 50 | 1 | 1 | 1.6 | 1.6 | 26 | 26 | 33.2 | 33.2 | 3103 | 3103 | 0.387 | 0.387 | 0.494 | 0.494 | 0.076 | 0.076 | 0.5 | 0.5 | 1.8 | 1.8
[15 empty] | 100300400070 | 100300400070 | [22 empty] | 4 Core | 70 | 70 | 1.1 | 1.1 | 2 | 2 | 30.5 | 30.5 | 39.2 | 39.2 | 4405 | 4405 | 0.268 | 0.268 | 0.342 | 0.342 | 0.075 | 0.075 | 0.349 | 0.349 | 1.2 | 1.2
[15 empty] | 100300400095 | 100300400095 | [22 empty] | 4 Core | 95 | 95 | 1.1 | 1.1 | 2 | 2 | 34.5 | 34.5 | 43.2 | 43.2 | 5653 | 5653 | 0.193 | 0.193 | 0.247 | 0.247 | 0.074 | 0.074 | 0.258 | 0.258 | 1.1 | 1.1
[15 empty] | 100300400120 | 100300400120 | [22 empty] | 4 Core | 120 | 120 | 1.2 | 1.2 | 2.5 | 2.5 | 38.5 | 38.5 | 48.6 | 48.6 | 7252 | 7252 | 0.153 | 0.153 | 0.196 | 0.196 | 0.072 | 0.072 | 0.209 | 0.209 | 0.76 | 0.76
[15 empty] | 100300400150 | 100300400150 | [22 empty] | 4 Core | 150 | 150 | 1.4 | 1.4 | 2.5 | 2.5 | 42.5 | 42.5 | 53 | 53 | 8553 | 8553 | 0.124 | 0.124 | 0.16 | 0.16 | 0.073 | 0.073 | 0.176 | 0.176 | 0.68 | 0.68
[15 empty] | 100300400185 | 100300400185 | [22 empty] | 4 Core | 185 | 185 | 1.6 | 1.6 | 2.5 | 2.5 | 47.5 | 47.5 | 58 | 58 | 10304 | 10304 | 0.0991 | 0.0991 | 0.128 | 0.128 | 0.073 | 0.073 | 0.148 | 0.148 | 0.61 | 0.61
[15 empty] | 100300400240 | 100300400240 | [22 empty] | 4 Core | 240 | 240 | 1.7 | 1.7 | 2.5 | 2.5 | 53.5 | 53.5 | 64.5 | 64.5 | 12895 | 12895 | 0.0754 | 0.0754 | 0.099 | 0.099 | 0.072 | 0.072 | 0.122 | 0.122 | 0.54 | 0.54
[15 empty] | 100300400300 | 100300400300 | [22 empty] | 4 Core | 300 | 300 | 1.8 | 1.8 | 2.5 | 2.5 | 59 | 59 | 70.3 | 70.3 | 15545 | 15545 | 0.0601 | 0.0601 | 0.08 | 0.08 | 0.072 | 0.072 | 0.107 | 0.107 | 0.49 | 0.49
[15 empty] | 100300400400 | 100300400400 | [22 empty] | 4 Core | 400 | 400 | 2 | 2 | 3.15 | 3.15 | 66.5 | 66.5 | 79.8 | 79.8 | 20245 | 20245 | 0.047 | 0.047 | 0.064 | 0.064 | 0.071 | 0.071 | 0.096 | 0.096 | 0.35 | 0.35
https://www.rrkabel.com/fire-security-cable/single-core-fire-resistant | SINGLE CORE FIRE RESISTANT | ['https://www.rrkabel.com/Uploads/Products/101/ProductZoomForMoreDetailsImage/Single-Core-Fire-Resistant.jpg', 'https://www.rrkabel.com/Uploads/Products/101/ProductZoomImage/03.jpg', 'https://www.rrkabel.com/Uploads/Products/301/ProductFeaturesDetails/01.png', 'https://www.rrkabel.com/Uploads/Products/301/ProductFeaturesDetails/01.png'] | ['These cables are designed for installations in trunking and conduits where a fire situation may pose a major hazard. Circuit integrity is maintained and to achieve optimum performance such cables should be installed in metal conduits.'] | ['Adapted to EN 50525-3-41'] | [57 empty] | ['450 / 750 V'] | ['-20°C to + 90°C (the cable should not be flexed when the temperature is below 0°C)'] | ['Stranded plain annealed copper conductor to BS EN 60228, class 2.'] | ['*Sheathed version also available. Details available on request.'] | ['BS 6387 categories C, W & Z (when applied to a single cable)', 'Exceeds IEC 60331 - 3 hours at 750°C - when the test temperature was increased to 950°C, equivalent to BS 6387 category C'] | ['IEC 60754-1, BS EN 50267-2-1'] | ['IEC 61034, BS EN 50268']
[15 empty] | 10040101xx60 | [26 empty] | 0.7 | [7 empty] | 32 | [18 empty] | 1.5 | 3.8
[15 empty] | 10040102xx60 | [26 empty] | 0.8 | [7 empty] | 43 | [18 empty] | 2.5 | 4.5
[15 empty] | 10040103xx60 | [26 empty] | 0.8 | [7 empty] | 55 | [18 empty] | 4 | 5
[15 empty] | 10040104xx60 | [26 empty] | 0.8 | [7 empty] | 85 | [18 empty] | 6 | 5.5
[15 empty] | 10040105xx60 | [26 empty] | 1 | [7 empty] | 146 | [18 empty] | 10 | 7
[15 empty] | 10040106xx60 | [26 empty] | 1 | [7 empty] | 198 | [18 empty] | 16 | 8
[15 empty] | 10040107xx60 | [26 empty] | 1.2 | [7 empty] | 320 | [18 empty] | 25 | 9.7
[15 empty] | 10040108xx60 | [26 empty] | 1.2 | [7 empty] | 410 | [18 empty] | 35 | 10.8
[15 empty] | 10040109xx60 | [26 empty] | 1.4 | [7 empty] | 549 | [18 empty] | 50 | 13.3
[15 empty] | 10040110xx60 | [26 empty] | 1.4 | [7 empty] | 770 | [18 empty] | 70 | 15.1
[15 empty] | 10040111xx60 | [26 empty] | 1.6 | [7 empty] | 1140 | [18 empty] | 95 | 17.5
[15 empty] | 10040112xx60 | [26 empty] | 1.6 | [7 empty] | 1425 | [18 empty] | 120 | 19.2
[15 empty] | 10040113xx60 | [26 empty] | 1.8 | [7 empty] | 1720 | [18 empty] | 150 | 21.2
[15 empty] | 10040114xx60 | [26 empty] | 2 | [7 empty] | 2155 | [18 empty] | 185 | 23.6
[71 empty] | 1 | 14 | 13 | 17 | 15 | 19 | 17.5 | – | – | – | – | –
[71 empty] | 1.5 | 19 | 17 | 23 | 20 | 25 | 23 | – | – | – | – | –
[71 empty] | 2.5 | 26 | 23 | 31 | 28 | 34 | 31 | – | – | – | – | –
[71 empty] | 4 | 35 | 31 | 42 | 37 | 46 | 41 | – | – | – | – | –
[71 empty] | 6 | 45 | 40 | 54 | 48 | 59 | 54 | – | – | – | – | –
[71 empty] | 10 | 61 | 54 | 75 | 66 | 81 | 74 | – | – | – | – | –
[71 empty] | 16 | 81 | 73 | 100 | 88 | 109 | 99 | – | – | – | – | –
[71 empty] | 25 | 106 | 95 | 133 | 117 | 143 | 130 | 161 | 141 | 135 | 182 | 161
[71 empty] | 35 | 131 | 117 | 164 | 144 | 176 | 161 | 200 | 176 | 169 | 226 | 201
[71 empty] | 50 | 158 | 141 | 198 | 175 | 228 | 209 | 242 | 216 | 207 | 275 | 246
[71 empty] | 70 | 200 | 179 | 253 | 222 | 293 | 268 | 310 | 279 | 268 | 353 | 318
[71 empty] | 95 | 241 | 216 | 306 | 269 | 355 | 326 | 377 | 342 | 328 | 430 | 389
[71 empty] | 120 | 278 | 249 | 354 | 312 | 413 | 379 | 437 | 400 | 383 | 500 | 454
[71 empty] | 150 | 318 | 285 | 393 | 342 | 476 | 436 | 504 | 464 | 444 | 577 | 527
[71 empty] | 185 | 362 | 324 | 449 | 384 | 545 | 500 | 575 | 533 | 510 | 661 | 605
[71 empty] | 240 | 424 | 380 | 528 | 450 | 644 | 590 | 679 | 634 | 607 | 781 | 719
[71 empty] | 300 | 486 | 435 | 603 | 514 | 743 | 681 | 783 | 736 | 703 | 902 | 833
[71 empty] | 400 | – | – | 683 | 584 | 868 | 793 | 940 | 868 | 823 | 1085 | 1008
[71 empty] | 500 | – | – | 783 | 666 | 990 | 904 | 1083 | 998 | 946 | 1253 | 1169
[71 empty] | 630 | – | – | 900 | 764 | 1130 | 1033 | 1254 | 1151 | 1088 | 1454 | 1362
[71 empty] | 800 | – | – | – | – | 1288 | 1179 | 1358 | 1275 | 1214 | 1581 | 1485
[71 empty] | 1000 | – | – | – | – | 1443 | 1323 | 1520 | 1436 | 1349 | 1775 | 1671
[71 empty] | 1 | [11 empty] | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40
[71 empty] | 1.5 | [11 empty] | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27
[71 empty] | 2.5 | [11 empty] | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16
[71 empty] | 4 | [11 empty] | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
[71 empty] | 6 | [11 empty] | 7.9 | 7.9 | 7.9 | 7.9 | 7.9 | 7.9 | 7.9 | 7.9 | 7.9 | 7.9 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8
[71 empty] | 10 | [11 empty] | 4.7 | 4.7 | 4.7 | 4.7 | 4.7 | 4.7 | 4.7 | 4.7 | 4.7 | 4.7 | 4.0 | 4.0 | 4.0 | 4.0 | 4.0 | 4.0 | 4.0 | 4.0 | 4.0 | 4.0 | 4.0 | 4.0
[71 empty] | 16 | [11 empty] | 2.9 | 2.9 | 2.9 | 2.9 | 2.9 | 2.9 | 2.9 | 2.9 | 2.9 | 2.9 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5
[84 empty] | r | x | z | r | x | z | r | x | z | r | x | z | r | x | z | r | x | z | r | x | z
[71 empty] | 25 | [11 empty] | 1.85 | 1.85 | 0.31 | 1.90 | 1.85 | 0.190 | 1.85 | 1.85 | 0.28 | 1.85 | 1.6 | 0.27 | 1.65 | 1.6 | 0.165 | 1.6 | 1.6 | 0.190 | 1.6 | 1.60 | 0.27 | 1.65
[71 empty] | 35 | [11 empty] | 1.35 | 1.35 | 0.29 | 1.35 | 1.35 | 0.180 | 1.35 | 1.35 | 0.27 | 1.35 | 1.15 | 0.25 | 1.15 | 1.15 | 0.155 | 1.15 | 1.15 | 0.180 | 1.15 | 1.15 | 0.26 | 1.2
[71 empty] | 50 | [11 empty] | 0.99 | 1.00 | 0.29 | 1.05 | 0.99 | 0.180 | 1.00 | 0.99 | 0.27 | 1.00 | 0.87 | 0.25 | 0.90 | 0.86 | 0.155 | 0.87 | 0.86 | 0.180 | 0.87 | 0.86 | 0.26 | 0.89
[71 empty] | 70 | [11 empty] | 0.68 | 0.70 | 0.28 | 0.75 | 0.68 | 0.175 | 0.71 | 0.68 | 0.26 | 0.73 | 0.6 | 0.24 | 0.65 | 0.59 | 0.150 | 0.61 | 0.59 | 0.175 | 0.62 | 0.56 | 0.25 | 0.65
[71 empty] | 95 | [11 empty] | 0.49 | 0.51 | 0.27 | 0.58 | 0.49 | 0.170 | 0.52 | 0.49 | 0.26 | 0.56 | 0.44 | 0.23 | 0.5 | 0.43 | 0.145 | 0.45 | 0.43 | 0.170 | 0.46 | 0.43 | 0.25 | 0.49
[71 empty] | 120 | [11 empty] | 0.39 | 0.41 | 0.26 | 0.48 | 0.39 | 0.165 | 0.43 | 0.39 | 0.25 | 0.47 | 0.35 | 0.23 | 0.42 | 0.34 | 0.140 | 0.37 | 0.34 | 0.165 | 0.38 | 0.34 | 0.24 | 0.42
[71 empty] | 150 | [11 empty] | 0.32 | 0.33 | 0.26 | 0.43 | 0.32 | 0.165 | 0.36 | 0.32 | 0.25 | 0.41 | 0.29 | 0.23 | 0.37 | 0.28 | 0.140 | 0.31 | 0.28 | 0.165 | 0.32 | 0.28 | 0.24 | 0.37
[71 empty] | 185 | [11 empty] | 0.25 | 0.27 | 0.26 | 0.37 | 0.26 | 0.165 | 0.30 | 0.25 | 0.25 | 0.36 | 0.23 | 0.23 | 0.32 | 0.22 | 0.140 | 0.26 | 0.22 | 0.165 | 0.24 | 0.170 | 0.24 | 0.29
[71 empty] | 240 | [11 empty] | 0.19 | 0.21 | 0.26 | 0.33 | 0.20 | 0.160 | 0.25 | 0.195 | 0.25 | 0.31 | 0.185 | 0.22 | 0.29 | 0.170 | 0.140 | 0.22 | 0.170 | 0.165 | 0.24 | 0.170 | 0.24 | 0.29
[71 empty] | 300 | [11 empty] | 0.155 | 0.175 | 0.25 | 0.31 | 0.160 | 0.160 | 0.22 | 0.155 | 0.25 | 0.29 | 0.150 | 0.22 | 0.27 | 0.140 | 0.140 | 0.195 | 0.135 | 0.160 | 0.21 | 0.135 | 0.24 | 0.26
[71 empty] | 400 | [11 empty] | 0.12 | 0.140 | 0.25 | 0.29 | 0.130 | 0.155 | 0.20 | 0.125 | 0.24 | 0.27 | 0.125 | 0.22 | 0.25 | 0.110 | 0.135 | 0.175 | 0.110 | 0.160 | 0.195 | 0.110 | 0.24 | 0.26
[71 empty] | 500 | [11 empty] | 0.093 | 0.120 | 0.25 | 0.29 | 0.105 | 0.155 | 0.185 | 0.098 | 0.24 | 0.26 | 0.100 | 0.22 | 0.24 | 0.090 | 0.135 | 0.160 | 0.880 | 0.160 | 0.180 | 0.085 | 0.24 | 0.25
[71 empty] | 630 | [11 empty] | 0.072 | 0.100 | 0.25 | 0.27 | 0.086 | 0.155 | 0.175 | 0.078 | 0.24 | 0.25 | 0.088 | 0.21 | 0.23 | 0.074 | 0.135 | 0.150 | 0.710 | 0.160 | 0.170 | 0680 | 0.23 | 0.24
[71 empty] | 800 | [11 empty] | 0.056 | – | – | – | 0.072 | 0.150 | 0.170 | 0.064 | 0.24 | 0.25 | – | – | – | 0.062 | 0.130 | 0.145 | 0.059 | 0.155 | 0.165 | 0.055 | 0.23 | 0.24
[71 empty] | 1000 | [11 empty] | 0.045 | – | – | – | 0.063 | 0.150 | 0.165 | 0.054 | 0.24 | 0.24 | – | – | – | 0.055 | 0.130 | 0.140 | 0.050 | 0.155 | 0.165 | 0.047 | 0.23 | 0.24