## Sheet1
Link | Title | Images | Standard | Conductor: | Insulation: | Pairs: | Identification Pairs: | Wrapping: | Collective Screen: | Cable Sheath: | Flame Propagation: | Operating Temperature Range: | Bending Radius: | Operating Voltage: | Electrical Properties | Conductor Cross Section (Sq.mm) | Class of Conductor | No. of Strands/Max. Strand Diameter (mm) | Max. DC Conductor Resistance* at 20°C (Ω/km) | Max.L/R Ratio (μH/Ω) | Min. Insulation Resistance (GΩ x cm) | Max. Mutual Capacitance (nF/km) | Max.Inductance (mH/km) | Test Voltage Vrms (Core-Core) | Test Voltage Vrms (Core-Screen) | Unnamed: 0 | Part Number | No. of Pairs and Nom.Cross Sectional Area (Sq. mm) | Min. InsulationThickness (mm) | Nominal SheathThickness (mm) | Approx. Cable Diameter (mm) | Approx. Cable Weight (kg/km) | Individual Screen: | Assembly: |  | Inner Sheath: | Armour: | Operating Temperature Range: | Bending Radius: | No. of Pairs and Nom. Cross Sectional Area(Sq. mm) | Min. Insulation Thickness (mm) | Nominal Inner Sheath Thickness (mm) | Approx. Dia.Over Inner Sheath (mm) | Nominal Dia. of Armour Wire (mm) | Nominal Outer Sheath Thickness (mm) | Approx. Cable Weight (kg/km | No. of Pairs and Nom. Cross Sectional Area (Sq. mm) | Nominal Dia. of Armour Wire(mm) | Conductor | Insulation | Pairs | Identification Pairs | Individual Screen | Assembly | Collective Screen | Inner Sheath | Armour | Cable Sheath | Flame Propagation | Operating Temperature Range | Bending Radius | Operating Voltage | Colour Code | Wrapping | Max. DC Conductor Resistance at 20°C (Ω/km) | Max. L/R Ratio (μH/Ω) | Max. Inductance (mH/km) | Test Voltage V rms (Core-Screen) | No. of Cores and Nom. Cross Sectional Area(Sq. mm) | Nominal Sheath Thickness (mm) | Colour Code: | Approx. Dia. Over InnerSheath (mm)
https://www.rrkabel.com/instrumentation-cable/instrumentation-cable-re-ysty-single-multi-pair | RE-Y(St)Y – SINGLE & MULTI-PAIR | ['https://www.rrkabel.com/Uploads/Products/79/ProductZoomForMoreDetailsImage/02.jpg', 'https://www.rrkabel.com/Uploads/Products/79/ProductZoomImage/03.jpg', 'https://www.rrkabel.com/Uploads/Products/235/ProductFeaturesDetails/01.png', 'https://www.rrkabel.com/Uploads/Products/235/ProductFeaturesDetails/01.png'] | ['Adapted to EN 50288-7.'] | ['Annealed copper wires according to BS EN 60228'] | ['Polyvinyl chloride PVC'] | ['Twisted'] | ['Black & white, continuously numbered on white core (1, 2, 3…) for multi-element'] | ['1 layer of PETP tape'] | ['Aluminium / PETP tape over tinned copper drain wire'] | ['Polyvinyl Chloride PVC'] | ['EN 60332-1-2'] | ['-30°C to +70°C'] | ['7.5 x cable diameter'] | ['500V', '*Also available in 300V variant on request'] | ['*For multi-pair maximum resistance shall be increased by 2%']
[16 empty] | 0.5 | 2 | 7/0.3 | 36 | 25 | 20 | 250 | 1 | 2000 | 2000
[16 empty] | 0.5 | 5 | 16/0.2 | 39 | 25 | 20 | 250 | 1 | 2000 | 2000
[16 empty] | 0.75 | 2 | 7/0.37 | 24.5 | 25 | 20 | 250 | 1 | 2000 | 2000
[16 empty] | 0.75 | 5 | 24/0.2 | 26 | 25 | 20 | 250 | 1 | 2000 | 2000
[16 empty] | 1 | 2 | 7/0.43 | 18.1 | 25 | 20 | 250 | 1 | 2000 | 2000
[16 empty] | 1 | 5 | 32/0.2 | 19.5 | 25 | 20 | 250 | 1 | 2000 | 2000
[16 empty] | 1.5 | 2 | 7/0.53 | 12.1 | 40 | 20 | 250 | 1 | 2000 | 2000
[16 empty] | 2.5 | 2 | 7/0.67 | 7.41 | 60 | 20 | 250 | 1 | 2000 | 2000
[26 empty] | Class 5 Conductor | 70150121050 | 1 x 2 x 0.5 | 0.44 | 1 | 6.4 | 48.2
[26 empty] | Class 5 Conductor | 70150221050 | 2 x 2 x 0.5 | 0.44 | 1 | 7.7 | 74.2
[26 empty] | Class 5 Conductor | 70150321050 | 3 x 2 x 0.5 | 0.44 | 1.1 | 9 | 100.8
[26 empty] | Class 5 Conductor | 70150421050 | 4 x 2 x 0.5 | 0.44 | 1.1 | 10.1 | 126.5
[26 empty] | Class 5 Conductor | 70150521050 | 5 x 2 x 0.5 | 0.44 | 1.2 | 11.1 | 151.8
[26 empty] | Class 5 Conductor | 70150821050 | 8 x 2 x 0.5 | 0.44 | 1.3 | 13.6 | 225.5
[26 empty] | Class 5 Conductor | 70151021050 | 10 x 2 x 0.5 | 0.44 | 1.3 | 15 | 274
[26 empty] | Class 5 Conductor | 70151221050 | 12 x 2 x 0.5 | 0.44 | 1.4 | 16.2 | 321.9
[26 empty] | Class 5 Conductor | 70151621050 | 16 x 2 x 0.5 | 0.44 | 1.4 | 18.4 | 416.1
[26 empty] | Class 5 Conductor | 70152021050 | 20 x 2 x 0.5 | 0.44 | 1.5 | 20.4 | 510
[26 empty] | Class 5 Conductor | 70152421050 | 24 x 2 x 0.5 | 0.44 | 1.6 | 22.2 | 603.1
[26 empty] | Class 5 Conductor | 70150121075 | 1 x 2 x 0.75 | 0.44 | 1 | 6.8 | 56.7
[26 empty] | Class 5 Conductor | 70150221075 | 2 x 2 x 0.75 | 0.44 | 1.1 | 8.3 | 89.5
[26 empty] | Class 5 Conductor | 70150321075 | 3 x 2 x 0.75 | 0.44 | 1.1 | 9.7 | 122.9
[26 empty] | Class 5 Conductor | 70150421075 | 4 x 2 x 0.75 | 0.44 | 1.2 | 10.9 | 155.8
[26 empty] | Class 5 Conductor | 70150521075 | 5 x 2 x 0.75 | 0.44 | 1.2 | 12 | 188
[26 empty] | Class 5 Conductor | 70150821075 | 8 x 2 x 0.75 | 0.44 | 1.3 | 14.7 | 282.2
[26 empty] | Class 5 Conductor | 70151021075 | 10 x 2 x 0.75 | 0.44 | 1.4 | 16.2 | 345
[26 empty] | Class 5 Conductor | 70151221075 | 12 x 2 x 0.75 | 0.44 | 1.4 | 17.6 | 406.3
[26 empty] | Class 5 Conductor | 70151621075 | 16 x 2 x 0.75 | 0.44 | 1.5 | 20 | 527.7
[26 empty] | Class 5 Conductor | 70152021075 | 20 x 2 x 0.75 | 0.44 | 1.6 | 22.2 | 649.5
[26 empty] | Class 5 Conductor | 70152421075 | 24 x 2 x 0.75 | 0.44 | 1.6 | 24.1 | 769
[26 empty] | Class 5 Conductor | 70150120001 | 1 x 2 x 1 | 0.44 | 1 | 7.1 | 64.1
[26 empty] | Class 5 Conductor | 70150220001 | 2 x 2 x 1 | 0.44 | 1.1 | 8.7 | 103.4
[26 empty] | Class 5 Conductor | 70150320001 | 3 x 2 x 1 | 0.44 | 1.1 | 10.2 | 143.1
[26 empty] | Class 5 Conductor | 70150420001 | 4 x 2 x 1 | 0.44 | 1.2 | 11.5 | 182.2
[26 empty] | Class 5 Conductor | 70150520001 | 5 x 2 x 1 | 0.44 | 1.2 | 12.6 | 220.5
[26 empty] | Class 5 Conductor | 70150820001 | 8 x 2 x 1 | 0.44 | 1.3 | 15.5 | 333.8
[26 empty] | Class 5 Conductor | 70151020001 | 10 x 2 x 1 | 0.44 | 1.4 | 17.1 | 408.9
[26 empty] | Class 5 Conductor | 70151220001 | 12 x 2 x 1 | 0.44 | 1.4 | 18.6 | 482.3
[26 empty] | Class 5 Conductor | 70151620001 | 16 x 2 x 1 | 0.44 | 1.5 | 21.2 | 629
[26 empty] | Class 5 Conductor | 70152020001 | 20 x 2 x 1 | 0.44 | 1.6 | 23.5 | 776.5
[26 empty] | Class 5 Conductor | 70152420001 | 24 x 2 x 1 | 0.44 | 1.7 | 25.5 | 920.3
[26 empty] | Class 2 Conductor | 70120121050 | 1 x 2 x 0.5 | 0.44 | 1 | 6.4 | 48
[26 empty] | Class 2 Conductor | 70120221050 | 2 x 2 x 0.5 | 0.44 | 1 | 7.7 | 73.9
[26 empty] | Class 2 Conductor | 70120321050 | 3 x 2 x 0.5 | 0.44 | 1.1 | 9 | 100.4
[26 empty] | Class 2 Conductor | 70120421050 | 4 x 2 x 0.5 | 0.44 | 1.1 | 10.1 | 125.9
[26 empty] | Class 2 Conductor | 70120521050 | 5 x 2 x 0.5 | 0.44 | 1.2 | 11.1 | 151.2
[26 empty] | Class 2 Conductor | 70120821050 | 8 x 2 x 0.5 | 0.44 | 1.3 | 13.6 | 224.5
[26 empty] | Class 2 Conductor | 70121021050 | 10 x 2 x 0.5 | 0.44 | 1.3 | 15 | 272.7
[26 empty] | Class 2 Conductor | 70121221050 | 12 x 2 x 0.5 | 0.44 | 1.4 | 16.2 | 320.4
[26 empty] | Class 2 Conductor | 70121621050 | 16 x 2 x 0.5 | 0.44 | 1.4 | 18.4 | 414.1
[26 empty] | Class 2 Conductor | 70122021050 | 20 x 2 x 0.5 | 0.44 | 1.5 | 20.4 | 507.5
[26 empty] | Class 2 Conductor | 70122421050 | 24 x 2 x 0.5 | 0.44 | 1.6 | 22.2 | 600.1
[26 empty] | Class 2 Conductor | 70120121075 | 1 x 2 x 0.75 | 0.44 | 1 | 6.8 | 56.7
[26 empty] | Class 2 Conductor | 70120221075 | 2 x 2 x 0.75 | 0.44 | 1.1 | 8.3 | 89.5
[26 empty] | Class 2 Conductor | 70120321075 | 3 x 2 x 0.75 | 0.44 | 1.1 | 9.7 | 123.4
[26 empty] | Class 2 Conductor | 70120421075 | 4 x 2 x 0.75 | 0.44 | 1.2 | 10.9 | 155.9
[26 empty] | Class 2 Conductor | 70120521075 | 5 x 2 x 0.75 | 0.44 | 1.2 | 12 | 188
[26 empty] | Class 2 Conductor | 70120821075 | 8 x 2 x 0.75 | 0.44 | 1.3 | 14.7 | 282.4
[26 empty] | Class 2 Conductor | 70121021075 | 10 x 2 x 0.75 | 0.44 | 1.4 | 16.3 | 345.1
[26 empty] | Class 2 Conductor | 70121221075 | 12 x 2 x 0.75 | 0.44 | 1.4 | 17.6 | 406.4
[26 empty] | Class 2 Conductor | 70121621075 | 16 x 2 x 0.75 | 0.44 | 1.5 | 20.1 | 527.9
[26 empty] | Class 2 Conductor | 70122021075 | 20 x 2 x 0.75 | 0.44 | 1.6 | 22.2 | 649.7
[26 empty] | Class 2 Conductor | 70122421075 | 24 x 2 x 0.75 | 0.44 | 1.6 | 24.2 | 769.4
[26 empty] | Class 2 Conductor | 70120120001 | 1 x 2 x 1 | 0.44 | 1 | 7.2 | 65.2
[26 empty] | Class 2 Conductor | 70120220001 | 2 x 2 x 1 | 0.44 | 1.1 | 8.8 | 105.6
[26 empty] | Class 2 Conductor | 70120320001 | 3 x 2 x 1 | 0.44 | 1.1 | 10.4 | 146.7
[26 empty] | Class 2 Conductor | 70120420001 | 4 x 2 x 1 | 0.44 | 1.2 | 11.7 | 186.8
[26 empty] | Class 2 Conductor | 70120520001 | 5 x 2 x 1 | 0.44 | 1.2 | 12.9 | 226.1
[26 empty] | Class 2 Conductor | 70120820001 | 8 x 2 x 1 | 0.44 | 1.3 | 15.8 | 342.3
[26 empty] | Class 2 Conductor | 70121020001 | 10 x 2 x 1 | 0.44 | 1.4 | 17.4 | 419.3
[26 empty] | Class 2 Conductor | 70121220001 | 12 x 2 x 1 | 0.44 | 1.5 | 19 | 495.5
[26 empty] | Class 2 Conductor | 70121620001 | 16 x 2 x 1 | 0.44 | 1.6 | 21.6 | 646
[26 empty] | Class 2 Conductor | 70122020001 | 20 x 2 x 1 | 0.44 | 1.6 | 23.9 | 796.2
[26 empty] | Class 2 Conductor | 70122420001 | 24 x 2 x 1 | 0.44 | 1.7 | 26 | 945
[26 empty] | Class 2 Conductor | 70120121105 | 1 x 2 x 1.5 | 0.44 | 1 | 7.9 | 81.9
[26 empty] | Class 2 Conductor | 70120221105 | 2 x 2 x 1.5 | 0.44 | 1.1 | 9.7 | 136.4
[26 empty] | Class 2 Conductor | 70120321105 | 3 x 2 x 1.5 | 0.44 | 1.2 | 11.5 | 191.5
[26 empty] | Class 2 Conductor | 70120421105 | 4 x 2 x 1.5 | 0.44 | 1.2 | 13 | 246
[26 empty] | Class 2 Conductor | 70120521105 | 5 x 2 x 1.5 | 0.44 | 1.3 | 14.3 | 299.7
[26 empty] | Class 2 Conductor | 70120821105 | 8 x 2 x 1.5 | 0.44 | 1.4 | 17.7 | 457.6
[26 empty] | Class 2 Conductor | 70121021105 | 10 x 2 x 1.5 | 0.44 | 1.5 | 19.5 | 563.2
[26 empty] | Class 2 Conductor | 70121221105 | 12 x 2 x 1.5 | 0.44 | 1.5 | 21.2 | 666.6
[26 empty] | Class 2 Conductor | 70121621105 | 16 x 2 x 1.5 | 0.44 | 1.6 | 24.2 | 872.3
[26 empty] | Class 2 Conductor | 70122021105 | 20 x 2 x 1.5 | 0.44 | 1.7 | 26.8 | 1079.7
[26 empty] | Class 2 Conductor | 70122421105 | 24 x 2 x 1.5 | 0.44 | 1.8 | 29.2 | 1283.9
[26 empty] | Class 2 Conductor | 70120121205 | 1 x 2 x 2.5 | 0.53 | 1.1 | 9.3 | 113.8
[26 empty] | Class 2 Conductor | 70120221205 | 2 x 2 x 2.5 | 0.53 | 1.2 | 11.5 | 195.3
[26 empty] | Class 2 Conductor | 70120321205 | 3 x 2 x 2.5 | 0.53 | 1.3 | 13.6 | 278.3
[26 empty] | Class 2 Conductor | 70120421205 | 4 x 2 x 2.5 | 0.53 | 1.3 | 15.5 | 360.2
[26 empty] | Class 2 Conductor | 70120521205 | 5 x 2 x 2.5 | 0.53 | 1.4 | 17.1 | 441.1
[26 empty] | Class 2 Conductor | 70120821205 | 8 x 2 x 2.5 | 0.53 | 1.5 | 21.1 | 680.6
[26 empty] | Class 2 Conductor | 70121021205 | 10 x 2 x 2.5 | 0.53 | 1.6 | 23.4 | 840.3
[26 empty] | Class 2 Conductor | 70121221205 | 12 x 2 x 2.5 | 0.53 | 1.7 | 25.5 | 998.3
[26 empty] | Class 2 Conductor | 70121621205 | 16 x 2 x 2.5 | 0.53 | 1.8 | 29.1 | 1310.9
[26 empty] | Class 2 Conductor | 70122021205 | 20 x 2 x 2.5 | 0.53 | 1.9 | 32.3 | 1627.1
[26 empty] | Class 2 Conductor | 70122421205 | 24 x 2 x 2.5 | 0.53 | 2.1 | 35.2 | 1938.7
https://www.rrkabel.com/instrumentation-cable/instrumentation-cable-re-ysty-pimf-multi-pair | RE-Y(St)Y PiMF – MULTI-PAIR | ['https://www.rrkabel.com/Uploads/Products/80/ProductZoomForMoreDetailsImage/02.jpg', 'https://www.rrkabel.com/Uploads/Products/80/ProductZoomImage/03.jpg', 'https://www.rrkabel.com/Uploads/Products/238/ProductFeaturesDetails/01.png', 'https://www.rrkabel.com/Uploads/Products/238/ProductFeaturesDetails/01.png'] | ['Adapted to EN 50288-7'] | ['Annealed copper wires according to BS EN 60228'] | ['Polyvinyl Chloride PVC'] | ['Twisted'] | ['Black & white, continuously numbered on white core (1, 2, 3…) for multi-element'] |  | ['Aluminium / PETP tape over tinned copper drain wire'] | ['Polyvinyl chloride PVC'] |  | ['-30°C to +70°C Bending Radius : 7.5 x cable diameter'] |  | ['500V', '*Also available in 300V variant on request.'] | ['*For multi-pair maximum resistance shall be increased by 2%'] | [17 empty] | ['Aluminium / PETP tape over tinned copper drain wire, plastic tape under and above screen'] | ['Concentric layers'] | ['strong>Flame Propagation: EN 60332-1-2']
[16 empty] | 0.5 | 2 | 7/0.3 | 36.7 | 25 | 20 | 250 | 1 | 2000 | 2000
[16 empty] | 0.5 | 5 | 16/0.2 | 39.8 | 25 | 20 | 250 | 1 | 2000 | 2000
[16 empty] | 0.75 | 2 | 7/0.37 | 25 | 25 | 20 | 250 | 1 | 2000 | 2000
[16 empty] | 0.75 | 5 | 24/0.2 | 26.5 | 25 | 20 | 250 | 1 | 2000 | 2000
[16 empty] | 1 | 2 | 7/0.43 | 18.5 | 25 | 20 | 250 | 1 | 2000 | 2000
[16 empty] | 1 | 5 | 32/0.2 | 19.9 | 25 | 20 | 250 | 1 | 2000 | 2000
[16 empty] | 1.5 | 2 | 7/0.53 | 12.3 | 40 | 20 | 250 | 1 | 2000 | 2000
[16 empty] | 2.5 | 2 | 7/0.67 | 7.6 | 60 | 20 | 250 | 1 | 2000 | 2000
[26 empty] | Class 5 Conductor | 70250221050 | 2 x 2 x 0.5 | 0.44 | 1.1 | 8.1 | 77
[26 empty] | Class 5 Conductor | 70250321050 | 3 x 2 x 0.5 | 0.44 | 1.1 | 9.7 | 104.8
[26 empty] | Class 5 Conductor | 70250421050 | 4 x 2 x 0.5 | 0.44 | 1.2 | 11 | 132.3
[26 empty] | Class 5 Conductor | 70250521050 | 5 x 2 x 0.5 | 0.44 | 1.2 | 12.2 | 159.7
[26 empty] | Class 5 Conductor | 70250821050 | 8 x 2 x 0.5 | 0.44 | 1.3 | 15.3 | 239.4
[26 empty] | Class 5 Conductor | 70251021050 | 10 x 2 x 0.5 | 0.44 | 1.4 | 17.1 | 292.9
[26 empty] | Class 5 Conductor | 70251221050 | 12 x 2 x 0.5 | 0.44 | 1.4 | 18.8 | 345.5
[26 empty] | Class 5 Conductor | 70251621050 | 16 x 2 x 0.5 | 0.44 | 1.6 | 21.9 | 451.5
[26 empty] | Class 5 Conductor | 70252021050 | 20 x 2 x 0.5 | 0.44 | 1.7 | 24.7 | 557.4
[26 empty] | Class 5 Conductor | 70252421050 | 24 x 2 x 0.5 | 0.44 | 1.8 | 27.3 | 663.8
[26 empty] | Class 5 Conductor | 70250221075 | 2 x 2 x 0.75 | 0.44 | 1.1 | 8.7 | 92.4
[26 empty] | Class 5 Conductor | 70250321075 | 3 x 2 x 0.75 | 0.44 | 1.1 | 10.4 | 127.6
[26 empty] | Class 5 Conductor | 70250421075 | 4 x 2 x 0.75 | 0.44 | 1.2 | 11.8 | 161.9
[26 empty] | Class 5 Conductor | 70250521075 | 5 x 2 x 0.75 | 0.44 | 1.2 | 13.1 | 196.1
[26 empty] | Class 5 Conductor | 70250821075 | 8 x 2 x 0.75 | 0.44 | 1.4 | 16.4 | 296.8
[26 empty] | Class 5 Conductor | 70251021075 | 10 x 2 x 0.75 | 0.44 | 1.4 | 18.4 | 364.9
[26 empty] | Class 5 Conductor | 70251221075 | 12 x 2 x 0.75 | 0.44 | 1.5 | 20.2 | 431
[26 empty] | Class 5 Conductor | 70251621075 | 16 x 2 x 0.75 | 0.44 | 1.6 | 23.5 | 563.9
[26 empty] | Class 5 Conductor | 70252021075 | 20 x 2 x 0.75 | 0.44 | 1.7 | 26.5 | 699.6
[26 empty] | Class 5 Conductor | 70252421075 | 24 x 2 x 0.75 | 0.44 | 1.8 | 29.3 | 833.1
[26 empty] | Class 5 Conductor | 70250220001 | 2 x 2 x 1 | 0.44 | 1.1 | 9.1 | 105.9
[26 empty] | Class 5 Conductor | 70250320001 | 3 x 2 x 1 | 0.44 | 1.2 | 10.9 | 147.9
[26 empty] | Class 5 Conductor | 70250420001 | 4 x 2 x 1 | 0.44 | 1.2 | 12.4 | 188.4
[26 empty] | Class 5 Conductor | 70250520001 | 5 x 2 x 1 | 0.44 | 1.3 | 13.7 | 228.9
[26 empty] | Class 5 Conductor | 70250820001 | 8 x 2 x 1 | 0.44 | 1.4 | 17.2 | 348.8
[26 empty] | Class 5 Conductor | 70251020001 | 10 x 2 x 1 | 0.44 | 1.5 | 19.3 | 429.4
[26 empty] | Class 5 Conductor | 70251220001 | 12 x 2 x 1 | 0.44 | 1.5 | 21.2 | 508.8
[26 empty] | Class 5 Conductor | 70251620001 | 16 x 2 x 1 | 0.44 | 1.7 | 24.7 | 667.6
[26 empty] | Class 5 Conductor | 70252020001 | 20 x 2 x 1 | 0.44 | 1.8 | 27.8 | 828.6
[26 empty] | Class 5 Conductor | 70252420001 | 24 x 2 x 1 | 0.44 | 1.9 | 30.7 | 986.8
[26 empty] | Class 2 Conductor | 70220221050 | 2 x 2 x 0.5 | 0.44 | 1.1 | 8.1 | 76.7
[26 empty] | Class 2 Conductor | 70220321050 | 3 x 2 x 0.5 | 0.44 | 1.1 | 9.7 | 104.4
[26 empty] | Class 2 Conductor | 70220421050 | 4 x 2 x 0.5 | 0.44 | 1.2 | 11 | 131.8
[26 empty] | Class 2 Conductor | 70220521050 | 5 x 2 x 0.5 | 0.44 | 1.2 | 12.2 | 159
[26 empty] | Class 2 Conductor | 70220821050 | 8 x 2 x 0.5 | 0.44 | 1.3 | 15.3 | 238.4
[26 empty] | Class 2 Conductor | 70221021050 | 10 x 2 x 0.5 | 0.44 | 1.4 | 17.1 | 291.6
[26 empty] | Class 2 Conductor | 70221221050 | 12 x 2 x 0.5 | 0.44 | 1.4 | 18.8 | 344
[26 empty] | Class 2 Conductor | 70221621050 | 16 x 2 x 0.5 | 0.44 | 1.6 | 21.9 | 449.5
[26 empty] | Class 2 Conductor | 70222021050 | 20 x 2 x 0.5 | 0.44 | 1.7 | 24.7 | 555
[26 empty] | Class 2 Conductor | 70222421050 | 24 x 2 x 0.5 | 0.44 | 1.8 | 27.3 | 660.8
[26 empty] | Class 2 Conductor | 70220221075 | 2 x 2 x 0.75 | 0.44 | 1.1 | 8.7 | 92.4
[26 empty] | Class 2 Conductor | 70220321075 | 3 x 2 x 0.75 | 0.44 | 1.1 | 10.4 | 127.6
[26 empty] | Class 2 Conductor | 70220421075 | 4 x 2 x 0.75 | 0.44 | 1.2 | 11.8 | 162
[26 empty] | Class 2 Conductor | 70220521075 | 5 x 2 x 0.75 | 0.44 | 1.2 | 13.1 | 196.2
[26 empty] | Class 2 Conductor | 70220821075 | 8 x 2 x 0.75 | 0.44 | 1.4 | 16.4 | 296.9
[26 empty] | Class 2 Conductor | 70221021075 | 10 x 2 x 0.75 | 0.44 | 1.4 | 18.4 | 365
[26 empty] | Class 2 Conductor | 70221221075 | 12 x 2 x 0.75 | 0.44 | 1.5 | 20.2 | 431.2
[26 empty] | Class 2 Conductor | 70221621075 | 16 x 2 x 0.75 | 0.44 | 1.6 | 23.5 | 565.3
[26 empty] | Class 2 Conductor | 70222021075 | 20 x 2 x 0.75 | 0.44 | 1.7 | 26.5 | 699.9
[26 empty] | Class 2 Conductor | 70222421075 | 24 x 2 x 0.75 | 0.44 | 1.8 | 29.3 | 833.5
[26 empty] | Class 2 Conductor | 70220220001 | 2 x 2 x 1 | 0.44 | 1.1 | 9.3 | 108.5
[26 empty] | Class 2 Conductor | 70220320001 | 3 x 2 x 1 | 0.44 | 1.2 | 11 | 151
[26 empty] | Class 2 Conductor | 70220420001 | 4 x 2 x 1 | 0.44 | 1.2 | 12.6 | 193.1
[26 empty] | Class 2 Conductor | 70220520001 | 5 x 2 x 1 | 0.44 | 1.3 | 14 | 234.6
[26 empty] | Class 2 Conductor | 70220820001 | 8 x 2 x 1 | 0.44 | 1.4 | 17.5 | 357.5
[26 empty] | Class 2 Conductor | 70221020001 | 10 x 2 x 1 | 0.44 | 1.5 | 19.6 | 440.1
[26 empty] | Class 2 Conductor | 70221220001 | 12 x 2 x 1 | 0.44 | 1.5 | 21.5 | 521.4
[26 empty] | Class 2 Conductor | 70221620001 | 16 x 2 x 1 | 0.44 | 1.7 | 25 | 684
[26 empty] | Class 2 Conductor | 70222020001 | 20 x 2 x 1 | 0.44 | 1.8 | 28.2 | 848.9
[26 empty] | Class 2 Conductor | 70222420001 | 24 x 2 x 1 | 0.44 | 1.9 | 31.2 | 1012.4
[26 empty] | Class 2 Conductor | 70220221105 | 2 x 2 x 1.5 | 0.44 | 1.1 | 10.2 | 139
[26 empty] | Class 2 Conductor | 70220321105 | 3 x 2 x 1.5 | 0.44 | 1.2 | 12.2 | 196.6
[26 empty] | Class 2 Conductor | 70220421105 | 4 x 2 x 1.5 | 0.44 | 1.3 | 13.9 | 252.7
[26 empty] | Class 2 Conductor | 70220521105 | 5 x 2 x 1.5 | 0.44 | 1.3 | 15.4 | 308.7
[26 empty] | Class 2 Conductor | 70220821105 | 8 x 2 x 1.5 | 0.44 | 1.5 | 19.4 | 473.9
[26 empty] | Class 2 Conductor | 70221021105 | 10 x 2 x 1.5 | 0.44 | 1.6 | 21.7 | 585.5
[26 empty] | Class 2 Conductor | 70221221105 | 12 x 2 x 1.5 | 0.44 | 1.6 | 23.8 | 695.5
[26 empty] | Class 2 Conductor | 70221621105 | 16 x 2 x 1.5 | 0.44 | 1.8 | 27.7 | 914.4
[26 empty] | Class 2 Conductor | 70222021105 | 20 x 2 x 1.5 | 0.44 | 1.9 | 31.2 | 1136.7
[26 empty] | Class 2 Conductor | 70222421105 | 24 x 2 x 1.5 | 0.44 | 2 | 34.4 | 1357
[26 empty] | Class 2 Conductor | 70220221205 | 2 x 2 x 2.5 | 0.53 | 1.2 | 11.9 | 198.7
[26 empty] | Class 2 Conductor | 70220321205 | 3 x 2 x 2.5 | 0.53 | 1.3 | 14.3 | 283.3
[26 empty] | Class 2 Conductor | 70220421205 | 4 x 2 x 2.5 | 0.53 | 1.4 | 16.3 | 367.6
[26 empty] | Class 2 Conductor | 70220521205 | 5 x 2 x 2.5 | 0.53 | 1.4 | 18.2 | 451.1
[26 empty] | Class 2 Conductor | 70220821205 | 8 x 2 x 2.5 | 0.53 | 1.6 | 22.8 | 698.8
[26 empty] | Class 2 Conductor | 70221021205 | 10 x 2 x 2.5 | 0.53 | 1.7 | 25.5 | 865.5
[26 empty] | Class 2 Conductor | 70221221205 | 12 x 2 x 2.5 | 0.53 | 1.8 | 28 | 1029.7
[26 empty] | Class 2 Conductor | 70221621205 | 16 x 2 x 2.5 | 0.53 | 2 | 32.6 | 1358.9
[26 empty] | Class 2 Conductor | 70222021205 | 20 x 2 x 2.5 | 0.53 | 2.1 | 36.6 | 1692.1
[26 empty] | Class 2 Conductor | 70222421205 | 24 x 2 x 2.5 | 0.53 | 2.2 | 40.4 | 2022.3
https://www.rrkabel.com/instrumentation-cable/instrumentation-cable-re-2xsty-single-multi-pair | RE-2X(St)Y – SINGLE & MULTI-PAIR | ['https://www.rrkabel.com/Uploads/Products/81/ProductZoomForMoreDetailsImage/02.jpg', 'https://www.rrkabel.com/Uploads/Products/81/ProductZoomImage/03.jpg', 'https://www.rrkabel.com/Uploads/Products/241/ProductFeaturesDetails/01.png', 'https://www.rrkabel.com/Uploads/Products/241/ProductFeaturesDetails/01.png'] | ['Adapted to EN 50288-7'] |  | ['Crosslinked polyethylene XLPE'] | ['Twisted'] | ['Black & white, continuously numbered on white core (1, 2, 3…) for multi-element'] |  | ['Aluminium / PETP tape over tinned copper drain wire'] | ['Polyvinyl chloride PVC (Also available in halogen free construction on request.)'] | ['EN 60332-1-2'] | ['-30°C to +90°C'] | ['7.5 x cable diameter'] | ['500V', '*Also available in 300V variant on request.'] | ['*For multi-pair maximum resistance shall be increased by 2%.'] | [19 empty] | ['strong>Conductor: Annealed copper wires according to BS EN 60228']
[16 empty] | 0.5 | 2 | 7/0.3 | 36 | 25 | 5000 | 150 | 1 | 2000 | 2000
[16 empty] | 0.5 | 5 | 16/0.2 | 39 | 25 | 5000 | 150 | 1 | 2000 | 2000
[16 empty] | 0.75 | 2 | 7/0.37 | 24.5 | 25 | 5000 | 150 | 1 | 2000 | 2000
[16 empty] | 0.75 | 5 | 24/0.2 | 26 | 25 | 5000 | 150 | 1 | 2000 | 2000
[16 empty] | 1 | 2 | 7/0.43 | 18.1 | 25 | 5000 | 150 | 1 | 2000 | 2000
[16 empty] | 1 | 5 | 32/0.2 | 19.5 | 25 | 5000 | 150 | 1 | 2000 | 2000
[16 empty] | 1.5 | 2 | 7/0.53 | 12.1 | 40 | 5000 | 150 | 1 | 2000 | 2000
[16 empty] | 2.5 | 2 | 7/0.67 | 7.41 | 60 | 5000 | 150 | 1 | 2000 | 2000
[26 empty] | Class 5 Conductor | 70350121050 | 1 x 2 x 0.5 | 0.44 | 1 | 6.4 | 45.1
[26 empty] | Class 5 Conductor | 70350221050 | 2 x 2 x 0.5 | 0.44 | 1 | 7.7 | 67.9
[26 empty] | Class 5 Conductor | 70350321050 | 3 x 2 x 0.5 | 0.44 | 1.1 | 9 | 91.3
[26 empty] | Class 5 Conductor | 70350421050 | 4 x 2 x 0.5 | 0.44 | 1.1 | 10.1 | 113.8
[26 empty] | Class 5 Conductor | 70350521050 | 5 x 2 x 0.5 | 0.44 | 1.2 | 11.1 | 136
[26 empty] | Class 5 Conductor | 70350821050 | 8 x 2 x 0.5 | 0.44 | 1.3 | 13.6 | 200.1
[26 empty] | Class 5 Conductor | 70351021050 | 10 x 2 x 0.5 | 0.44 | 1.3 | 15 | 242.3
[26 empty] | Class 5 Conductor | 70351221050 | 12 x 2 x 0.5 | 0.44 | 1.4 | 16.2 | 283.9
[26 empty] | Class 5 Conductor | 70351621050 | 16 x 2 x 0.5 | 0.44 | 1.4 | 18.4 | 365.3
[26 empty] | Class 5 Conductor | 70352021050 | 20 x 2 x 0.5 | 0.44 | 1.5 | 20.4 | 446.6
[26 empty] | Class 5 Conductor | 70352421050 | 24 x 2 x 0.5 | 0.44 | 1.6 | 22.2 | 527.1
[26 empty] | Class 5 Conductor | 70350121075 | 1 x 2 x 0.75 | 0.44 | 1 | 6.8 | 53.1
[26 empty] | Class 5 Conductor | 70350221075 | 2 x 2 x 0.75 | 0.44 | 1.1 | 8.3 | 82.2
[26 empty] | Class 5 Conductor | 70350321075 | 3 x 2 x 0.75 | 0.44 | 1.1 | 9.7 | 112
[26 empty] | Class 5 Conductor | 70350421075 | 4 x 2 x 0.75 | 0.44 | 1.2 | 10.9 | 141.3
[26 empty] | Class 5 Conductor | 70350521075 | 5 x 2 x 0.75 | 0.44 | 1.2 | 12 | 169.8
[26 empty] | Class 5 Conductor | 70350821075 | 8 x 2 x 0.75 | 0.44 | 1.3 | 14.7 | 253.1
[26 empty] | Class 5 Conductor | 70351021075 | 10 x 2 x 0.75 | 0.44 | 1.4 | 16.2 | 308.6
[26 empty] | Class 5 Conductor | 70351221075 | 12 x 2 x 0.75 | 0.44 | 1.4 | 17.6 | 362.6
[26 empty] | Class 5 Conductor | 70351621075 | 16 x 2 x 0.75 | 0.44 | 1.5 | 20 | 469.5
[26 empty] | Class 5 Conductor | 70352021075 | 20 x 2 x 0.75 | 0.44 | 1.6 | 22.2 | 576.7
[26 empty] | Class 5 Conductor | 70352421075 | 24 x 2 x 0.75 | 0.44 | 1.6 | 24.1 | 681.7
[26 empty] | Class 5 Conductor | 70350120001 | 1 x 2 x 1 | 0.44 | 1 | 7.1 | 60.1
[26 empty] | Class 5 Conductor | 70350220001 | 2 x 2 x 1 | 0.44 | 1.1 | 8.7 | 95.5
[26 empty] | Class 5 Conductor | 70350320001 | 3 x 2 x 1 | 0.44 | 1.1 | 10.2 | 131.2
[26 empty] | Class 5 Conductor | 70350420001 | 4 x 2 x 1 | 0.44 | 1.2 | 11.5 | 166.3
[26 empty] | Class 5 Conductor | 70350520001 | 5 x 2 x 1 | 0.44 | 1.2 | 12.6 | 200.6
[26 empty] | Class 5 Conductor | 70350820001 | 8 x 2 x 1 | 0.44 | 1.3 | 15.5 | 302
[26 empty] | Class 5 Conductor | 70351020001 | 10 x 2 x 1 | 0.44 | 1.4 | 17.1 | 369.2
[26 empty] | Class 5 Conductor | 70351220001 | 12 x 2 x 1 | 0.44 | 1.4 | 18.6 | 434.7
[26 empty] | Class 5 Conductor | 70351620001 | 16 x 2 x 1 | 0.44 | 1.5 | 21.2 | 565.4
[26 empty] | Class 5 Conductor | 70352020001 | 20 x 2 x 1 | 0.44 | 1.6 | 23.5 | 697.1
[26 empty] | Class 5 Conductor | 70352420001 | 24 x 2 x 1 | 0.44 | 1.7 | 25.5 | 825
[26 empty] | Class 2 Conductor | 70320121050 | 1 x 2 x 0.5 | 0.44 | 1 | 6.4 | 44.9
[26 empty] | Class 2 Conductor | 70320221050 | 2 x 2 x 0.5 | 0.44 | 1 | 7.7 | 67.6
[26 empty] | Class 2 Conductor | 70320321050 | 3 x 2 x 0.5 | 0.44 | 1.1 | 9 | 90.8
[26 empty] | Class 2 Conductor | 70320421050 | 4 x 2 x 0.5 | 0.44 | 1.1 | 10.1 | 113.2
[26 empty] | Class 2 Conductor | 70320521050 | 5 x 2 x 0.5 | 0.44 | 1.2 | 11.1 | 135.3
[26 empty] | Class 2 Conductor | 70320821050 | 8 x 2 x 0.5 | 0.44 | 1.3 | 13.6 | 199
[26 empty] | Class 2 Conductor | 70321021050 | 10 x 2 x 0.5 | 0.44 | 1.3 | 15 | 240.9
[26 empty] | Class 2 Conductor | 70321221050 | 12 x 2 x 0.5 | 0.44 | 1.4 | 16.2 | 282.3
[26 empty] | Class 2 Conductor | 70321621050 | 16 x 2 x 0.5 | 0.44 | 1.4 | 18.4 | 363.2
[26 empty] | Class 2 Conductor | 70322021050 | 20 x 2 x 0.5 | 0.44 | 1.5 | 20.4 | 443.9
[26 empty] | Class 2 Conductor | 70322421050 | 24 x 2 x 0.5 | 0.44 | 1.6 | 22.2 | 523.9
[26 empty] | Class 2 Conductor | 70320121075 | 1 x 2 x 0.75 | 0.44 | 1 | 6.8 | 53
[26 empty] | Class 2 Conductor | 70320221075 | 2 x 2 x 0.75 | 0.44 | 1.1 | 8.3 | 82.2
[26 empty] | Class 2 Conductor | 70320321075 | 3 x 2 x 0.75 | 0.44 | 1.1 | 9.7 | 112.4
[26 empty] | Class 2 Conductor | 70320421075 | 4 x 2 x 0.75 | 0.44 | 1.2 | 10.9 | 141.2
[26 empty] | Class 2 Conductor | 70320521075 | 5 x 2 x 0.75 | 0.44 | 1.2 | 12 | 169.7
[26 empty] | Class 2 Conductor | 70320821075 | 8 x 2 x 0.75 | 0.44 | 1.3 | 14.7 | 253
[26 empty] | Class 2 Conductor | 70321021075 | 10 x 2 x 0.75 | 0.44 | 1.4 | 16.3 | 308.4
[26 empty] | Class 2 Conductor | 70321221075 | 12 x 2 x 0.75 | 0.44 | 1.4 | 17.6 | 362.4
[26 empty] | Class 2 Conductor | 70321621075 | 16 x 2 x 0.75 | 0.44 | 1.5 | 20.1 | 469.2
[26 empty] | Class 2 Conductor | 70322021075 | 20 x 2 x 0.75 | 0.44 | 1.6 | 22.2 | 576.3
[26 empty] | Class 2 Conductor | 70322421075 | 24 x 2 x 0.75 | 0.44 | 1.6 | 24.2 | 681.2
[26 empty] | Class 2 Conductor | 70320120001 | 1 x 2 x 1 | 0.44 | 1 | 7.2 | 61.1
[26 empty] | Class 2 Conductor | 70320220001 | 2 x 2 x 1 | 0.44 | 1.1 | 8.8 | 97.2
[26 empty] | Class 2 Conductor | 70320320001 | 3 x 2 x 1 | 0.44 | 1.1 | 10.4 | 134.2
[26 empty] | Class 2 Conductor | 70320420001 | 4 x 2 x 1 | 0.44 | 1.2 | 11.7 | 170.1
[26 empty] | Class 2 Conductor | 70320520001 | 5 x 2 x 1 | 0.44 | 1.2 | 12.9 | 205.2
[26 empty] | Class 2 Conductor | 70320820001 | 8 x 2 x 1 | 0.44 | 1.3 | 15.8 | 308.9
[26 empty] | Class 2 Conductor | 70321020001 | 10 x 2 x 1 | 0.44 | 1.4 | 17.4 | 377.7
[26 empty] | Class 2 Conductor | 70321220001 | 12 x 2 x 1 | 0.44 | 1.5 | 19 | 445.5
[26 empty] | Class 2 Conductor | 70321620001 | 16 x 2 x 1 | 0.44 | 1.6 | 21.6 | 579.4
[26 empty] | Class 2 Conductor | 70322020001 | 20 x 2 x 1 | 0.44 | 1.6 | 23.9 | 712.9
[26 empty] | Class 2 Conductor | 70322420001 | 24 x 2 x 1 | 0.44 | 1.7 | 26 | 845
[26 empty] | Class 2 Conductor | 70320121105 | 1 x 2 x 1.5 | 0.44 | 1 | 7.9 | 76.8
[26 empty] | Class 2 Conductor | 70320221105 | 2 x 2 x 1.5 | 0.44 | 1.1 | 9.7 | 126.3
[26 empty] | Class 2 Conductor | 70320321105 | 3 x 2 x 1.5 | 0.44 | 1.2 | 11.5 | 176.3
[26 empty] | Class 2 Conductor | 70320421105 | 4 x 2 x 1.5 | 0.44 | 1.2 | 13 | 225.7
[26 empty] | Class 2 Conductor | 70320521105 | 5 x 2 x 1.5 | 0.44 | 1.3 | 14.3 | 274.3
[26 empty] | Class 2 Conductor | 70320821105 | 8 x 2 x 1.5 | 0.44 | 1.4 | 17.7 | 417
[26 empty] | Class 2 Conductor | 70321021105 | 10 x 2 x 1.5 | 0.44 | 1.5 | 19.5 | 512.4
[26 empty] | Class 2 Conductor | 70321221105 | 12 x 2 x 1.5 | 0.44 | 1.5 | 21.2 | 605.6
[26 empty] | Class 2 Conductor | 70321621105 | 16 x 2 x 1.5 | 0.44 | 1.6 | 24.2 | 791
[26 empty] | Class 2 Conductor | 70322021105 | 20 x 2 x 1.5 | 0.44 | 1.7 | 26.8 | 978.1
[26 empty] | Class 2 Conductor | 70322421105 | 24 x 2 x 1.5 | 0.44 | 1.8 | 29.2 | 1162
[26 empty] | Class 2 Conductor | 70320121205 | 1 x 2 x 2.5 | 0.53 | 1.1 | 9.3 | 106.4
[26 empty] | Class 2 Conductor | 70320221205 | 2 x 2 x 2.5 | 0.53 | 1.2 | 11.5 | 180.6
[26 empty] | Class 2 Conductor | 70320321205 | 3 x 2 x 2.5 | 0.53 | 1.3 | 13.6 | 256.2
[26 empty] | Class 2 Conductor | 70320421205 | 4 x 2 x 2.5 | 0.53 | 1.3 | 15.5 | 330.7
[26 empty] | Class 2 Conductor | 70320521205 | 5 x 2 x 2.5 | 0.53 | 1.4 | 17.1 | 404.3
[26 empty] | Class 2 Conductor | 70320821205 | 8 x 2 x 2.5 | 0.53 | 1.5 | 21.1 | 621.6
[26 empty] | Class 2 Conductor | 70321021205 | 10 x 2 x 2.5 | 0.53 | 1.6 | 23.4 | 766.7
[26 empty] | Class 2 Conductor | 70321221205 | 12 x 2 x 2.5 | 0.53 | 1.7 | 25.5 | 909.9
[26 empty] | Class 2 Conductor | 70321621205 | 16 x 2 x 2.5 | 0.53 | 1.8 | 29.1 | 1193.1
[26 empty] | Class 2 Conductor | 70322021205 | 20 x 2 x 2.5 | 0.53 | 1.9 | 32.3 | 1479.8
[26 empty] | Class 2 Conductor | 70322421205 | 24 x 2 x 2.5 | 0.53 | 2.1 | 35.2 | 1762
https://www.rrkabel.com/instrumentation-cable/instrumentation-cable-re-re-2xsty-pimf-multi-pair | RE-2X(St)Y PiMF – MULTI-PAIR | ['https://www.rrkabel.com/Uploads/Products/82/ProductZoomForMoreDetailsImage/02.jpg', 'https://www.rrkabel.com/Uploads/Products/82/ProductZoomImage/03.jpg', 'https://www.rrkabel.com/Uploads/Products/244/ProductFeaturesDetails/01.png', 'https://www.rrkabel.com/Uploads/Products/244/ProductFeaturesDetails/01.png'] | ['Adapted to EN 50288-7'] | ['Annealed copper wires according to BS EN 60228'] | ['Crosslinked polyethylene XLPE'] | ['Twisted'] | ['Black & white, continuously numbered on white core (1, 2, 3…) for multi-element'] |  | ['Aluminium / PETP tape over tinned copper drain wire'] | ['Polyvinyl chloride PVC (Also available in halogen free construction on request.)'] | ['EN 60332-1-2'] | ['-30°C to +90°C'] | ['7.5 x cable diameter'] | ['500V', '*Also available in 300V variant on request.'] | [18 empty] | ['Aluminium / PETP tape over tinned copper drain wire, plastic tape under and above screen'] | ['Concentric layers']
[16 empty] | 0.5 | 2 | 7/0.3 | 36.7 | 25 | 5000 | 150 | 1 | 2000 | 2000
[16 empty] | 0.5 | 5 | 16/0.2 | 39.8 | 25 | 5000 | 150 | 1 | 2000 | 2000
[16 empty] | 0.75 | 2 | 7/0.37 | 25 | 25 | 5000 | 150 | 1 | 2000 | 2000
[16 empty] | 0.75 | 5 | 24/0.2 | 26.5 | 25 | 5000 | 150 | 1 | 2000 | 2000
[16 empty] | 1 | 2 | 7/0.43 | 18.5 | 25 | 5000 | 150 | 1 | 2000 | 2000
[16 empty] | 1 | 5 | 32/0.2 | 19.9 | 25 | 5000 | 150 | 1 | 2000 | 2000
[16 empty] | 1.5 | 2 | 7/0.53 | 12.3 | 40 | 5000 | 150 | 1 | 2000 | 2000
[16 empty] | 2.5 | 2 | 7/0.67 | 7.6 | 60 | 5000 | 150 | 1 | 2000 | 2000
[26 empty] | Class 5 Conductor | 70450221050 | 2 x 2 x 0.5 | 0.44 | 1.1 | 8.1 | 70.7
[26 empty] | Class 5 Conductor | 70450321050 | 3 x 2 x 0.5 | 0.44 | 1.1 | 9.7 | 95.3
[26 empty] | Class 5 Conductor | 70450421050 | 4 x 2 x 0.5 | 0.44 | 1.2 | 11 | 119.6
[26 empty] | Class 5 Conductor | 70450521050 | 5 x 2 x 0.5 | 0.44 | 1.2 | 12.2 | 143.9
[26 empty] | Class 5 Conductor | 70450821050 | 8 x 2 x 0.5 | 0.44 | 1.3 | 15.3 | 214.1
[26 empty] | Class 5 Conductor | 70451021050 | 10 x 2 x 0.5 | 0.44 | 1.4 | 17.1 | 261.2
[26 empty] | Class 5 Conductor | 70451221050 | 12 x 2 x 0.5 | 0.44 | 1.4 | 18.8 | 307.5
[26 empty] | Class 5 Conductor | 70451621050 | 16 x 2 x 0.5 | 0.44 | 1.6 | 21.9 | 400.8
[26 empty] | Class 5 Conductor | 70452021050 | 20 x 2 x 0.5 | 0.44 | 1.7 | 24.7 | 494.1
[26 empty] | Class 5 Conductor | 70452421050 | 24 x 2 x 0.5 | 0.44 | 1.8 | 27.3 | 587.8
[26 empty] | Class 5 Conductor | 70450221075 | 2 x 2 x 0.75 | 0.44 | 1.1 | 8.7 | 85.1
[26 empty] | Class 5 Conductor | 70450321075 | 3 x 2 x 0.75 | 0.44 | 1.1 | 10.4 | 116.6
[26 empty] | Class 5 Conductor | 70450421075 | 4 x 2 x 0.75 | 0.44 | 1.2 | 11.8 | 147.3
[26 empty] | Class 5 Conductor | 70450521075 | 5 x 2 x 0.75 | 0.44 | 1.2 | 13.1 | 177.9
[26 empty] | Class 5 Conductor | 70450821075 | 8 x 2 x 0.75 | 0.44 | 1.4 | 16.4 | 267.7
[26 empty] | Class 5 Conductor | 70451021075 | 10 x 2 x 0.75 | 0.44 | 1.4 | 18.4 | 328.5
[26 empty] | Class 5 Conductor | 70451221075 | 12 x 2 x 0.75 | 0.44 | 1.5 | 20.2 | 387.3
[26 empty] | Class 5 Conductor | 70451621075 | 16 x 2 x 0.75 | 0.44 | 1.6 | 23.5 | 505.6
[26 empty] | Class 5 Conductor | 70452021075 | 20 x 2 x 0.75 | 0.44 | 1.7 | 26.5 | 626.8
[26 empty] | Class 5 Conductor | 70452421075 | 24 x 2 x 0.75 | 0.44 | 1.8 | 29.3 | 745.7
[26 empty] | Class 5 Conductor | 70450220001 | 2 x 2 x 1 | 0.44 | 1.1 | 9.1 | 98
[26 empty] | Class 5 Conductor | 70450320001 | 3 x 2 x 1 | 0.44 | 1.2 | 10.9 | 135.9
[26 empty] | Class 5 Conductor | 70450420001 | 4 x 2 x 1 | 0.44 | 1.2 | 12.4 | 172.6
[26 empty] | Class 5 Conductor | 70450520001 | 5 x 2 x 1 | 0.44 | 1.3 | 13.7 | 209
[26 empty] | Class 5 Conductor | 70450820001 | 8 x 2 x 1 | 0.44 | 1.4 | 17.2 | 317
[26 empty] | Class 5 Conductor | 70451020001 | 10 x 2 x 1 | 0.44 | 1.5 | 19.3 | 389.7
[26 empty] | Class 5 Conductor | 70451220001 | 12 x 2 x 1 | 0.44 | 1.5 | 21.2 | 461.2
[26 empty] | Class 5 Conductor | 70451620001 | 16 x 2 x 1 | 0.44 | 1.7 | 24.7 | 604.1
[26 empty] | Class 5 Conductor | 70452020001 | 20 x 2 x 1 | 0.44 | 1.8 | 27.8 | 749.2
[26 empty] | Class 5 Conductor | 70452420001 | 24 x 2 x 1 | 0.44 | 1.9 | 30.7 | 891.5
[26 empty] | Class 2 Conductor | 70420221050 | 2 x 2 x 0.5 | 0.44 | 1.1 | 8.1 | 70.3
[26 empty] | Class 2 Conductor | 70420321050 | 3 x 2 x 0.5 | 0.44 | 1.1 | 9.7 | 94.9
[26 empty] | Class 2 Conductor | 70420421050 | 4 x 2 x 0.5 | 0.44 | 1.2 | 11 | 119.1
[26 empty] | Class 2 Conductor | 70420521050 | 5 x 2 x 0.5 | 0.44 | 1.2 | 12.2 | 143.1
[26 empty] | Class 2 Conductor | 70420821050 | 8 x 2 x 0.5 | 0.44 | 1.3 | 15.3 | 213
[26 empty] | Class 2 Conductor | 70421021050 | 10 x 2 x 0.5 | 0.44 | 1.4 | 17.1 | 259.9
[26 empty] | Class 2 Conductor | 70421221050 | 12 x 2 x 0.5 | 0.44 | 1.4 | 18.8 | 305.8
[26 empty] | Class 2 Conductor | 70421621050 | 16 x 2 x 0.5 | 0.44 | 1.6 | 21.9 | 398.6
[26 empty] | Class 2 Conductor | 70422021050 | 20 x 2 x 0.5 | 0.44 | 1.7 | 24.7 | 491.4
[26 empty] | Class 2 Conductor | 70422421050 | 24 x 2 x 0.5 | 0.44 | 1.8 | 27.3 | 584.6
[26 empty] | Class 2 Conductor | 70420221075 | 2 x 2 x 0.75 | 0.44 | 1.1 | 8.7 | 85
[26 empty] | Class 2 Conductor | 70420321075 | 3 x 2 x 0.75 | 0.44 | 1.1 | 10.4 | 116.6
[26 empty] | Class 2 Conductor | 70420421075 | 4 x 2 x 0.75 | 0.44 | 1.2 | 11.8 | 147.3
[26 empty] | Class 2 Conductor | 70420521075 | 5 x 2 x 0.75 | 0.44 | 1.2 | 13.1 | 177.8
[26 empty] | Class 2 Conductor | 70420821075 | 8 x 2 x 0.75 | 0.44 | 1.4 | 16.4 | 267.5
[26 empty] | Class 2 Conductor | 70421021075 | 10 x 2 x 0.75 | 0.44 | 1.4 | 18.4 | 328.3
[26 empty] | Class 2 Conductor | 70421221075 | 12 x 2 x 0.75 | 0.44 | 1.5 | 20.2 | 387.1
[26 empty] | Class 2 Conductor | 70421621075 | 16 x 2 x 0.75 | 0.44 | 1.6 | 23.5 | 506.5
[26 empty] | Class 2 Conductor | 70422021075 | 20 x 2 x 0.75 | 0.44 | 1.7 | 26.5 | 626.5
[26 empty] | Class 2 Conductor | 70422421075 | 24 x 2 x 0.75 | 0.44 | 1.8 | 29.3 | 745.3
[26 empty] | Class 2 Conductor | 70420220001 | 2 x 2 x 1 | 0.44 | 1.1 | 9.3 | 100.2
[26 empty] | Class 2 Conductor | 70420320001 | 3 x 2 x 1 | 0.44 | 1.2 | 11 | 138.5
[26 empty] | Class 2 Conductor | 70420420001 | 4 x 2 x 1 | 0.44 | 1.2 | 12.6 | 176.5
[26 empty] | Class 2 Conductor | 70420520001 | 5 x 2 x 1 | 0.44 | 1.3 | 14 | 213.7
[26 empty] | Class 2 Conductor | 70420820001 | 8 x 2 x 1 | 0.44 | 1.4 | 17.5 | 324.1
[26 empty] | Class 2 Conductor | 70421020001 | 10 x 2 x 1 | 0.44 | 1.5 | 19.6 | 398.4
[26 empty] | Class 2 Conductor | 70421220001 | 12 x 2 x 1 | 0.44 | 1.5 | 21.5 | 471.4
[26 empty] | Class 2 Conductor | 70421620001 | 16 x 2 x 1 | 0.44 | 1.7 | 25 | 617.4
[26 empty] | Class 2 Conductor | 70422020001 | 20 x 2 x 1 | 0.44 | 1.8 | 28.2 | 765.6
[26 empty] | Class 2 Conductor | 70422420001 | 24 x 2 x 1 | 0.44 | 1.9 | 31.2 | 912.4
[26 empty] | Class 2 Conductor | 70420221105 | 2 x 2 x 1.5 | 0.44 | 1.1 | 10.2 | 128.9
[26 empty] | Class 2 Conductor | 70420321105 | 3 x 2 x 1.5 | 0.44 | 1.2 | 12.2 | 181.4
[26 empty] | Class 2 Conductor | 70420421105 | 4 x 2 x 1.5 | 0.44 | 1.3 | 13.9 | 232.4
[26 empty] | Class 2 Conductor | 70420521105 | 5 x 2 x 1.5 | 0.44 | 1.3 | 15.4 | 283.3
[26 empty] | Class 2 Conductor | 70420821105 | 8 x 2 x 1.5 | 0.44 | 1.5 | 19.4 | 433.2
[26 empty] | Class 2 Conductor | 70421021105 | 10 x 2 x 1.5 | 0.44 | 1.6 | 21.7 | 534.7
[26 empty] | Class 2 Conductor | 70421221105 | 12 x 2 x 1.5 | 0.44 | 1.6 | 23.8 | 634.5
[26 empty] | Class 2 Conductor | 70421621105 | 16 x 2 x 1.5 | 0.44 | 1.8 | 27.7 | 833.2
[26 empty] | Class 2 Conductor | 70422021105 | 20 x 2 x 1.5 | 0.44 | 1.9 | 31.2 | 1035.1
[26 empty] | Class 2 Conductor | 70422421105 | 24 x 2 x 1.5 | 0.44 | 2 | 34.4 | 1235.1
[26 empty] | Class 2 Conductor | 70420221205 | 2 x 2 x 2.5 | 0.53 | 1.2 | 11.9 | 184
[26 empty] | Class 2 Conductor | 70420321205 | 3 x 2 x 2.5 | 0.53 | 1.3 | 14.3 | 261.2
[26 empty] | Class 2 Conductor | 70420421205 | 4 x 2 x 2.5 | 0.53 | 1.4 | 16.3 | 338.1
[26 empty] | Class 2 Conductor | 70420521205 | 5 x 2 x 2.5 | 0.53 | 1.4 | 18.2 | 414.3
[26 empty] | Class 2 Conductor | 70420821205 | 8 x 2 x 2.5 | 0.53 | 1.6 | 22.8 | 639.9
[26 empty] | Class 2 Conductor | 70421021205 | 10 x 2 x 2.5 | 0.53 | 1.7 | 25.5 | 791.8
[26 empty] | Class 2 Conductor | 70421221205 | 12 x 2 x 2.5 | 0.53 | 1.8 | 28 | 941.4
[26 empty] | Class 2 Conductor | 70421621205 | 16 x 2 x 2.5 | 0.53 | 2 | 32.6 | 1241.1
[26 empty] | Class 2 Conductor | 70422021205 | 20 x 2 x 2.5 | 0.53 | 2.1 | 36.6 | 1544.8
[26 empty] | Class 2 Conductor | 70422421205 | 24 x 2 x 2.5 | 0.53 | 2.2 | 40.4 | 1845.5
Class 2 Conductor
Class 2 Conductor
Class 2 Conductor
Class 2 Conductor
Class 2 Conductor
https://www.rrkabel.com/instrumentation-cable/instrumentation-cable-re-ystysway-single-multi-pair | RE-Y(St)YSWAY – SINGLE & MULTI-PAIR | ['https://www.rrkabel.com/Uploads/Products/83/ProductZoomForMoreDetailsImage/02.jpg', 'https://www.rrkabel.com/Uploads/Products/83/ProductZoomImage/03.jpg', 'https://www.rrkabel.com/Uploads/Products/247/ProductFeaturesDetails/01.png', 'https://www.rrkabel.com/Uploads/Products/247/ProductFeaturesDetails/01.png'] | ['Adapted to EN 50288-7'] | ['Annealed copper wires according to BS EN 60228'] | ['Polyvinyl chloride PVC'] | ['Twisted'] | ['Black & white, continuously numbered on white core (1, 2, 3…) for multi-element'] | ['1 layer of PETP tape'] | ['Aluminium / PETP tape over tinned copper drain wire'] | ['Polyvinyl chloride PVC'] | ['EN 60332-1-2'] |  |  | ['500V', '*Also available in 300V variant on request.'] | ['*For multi-pair maximum resistance shall be increased by 2%.'] | [20 empty] | ['Polyvinyl chloride PVC'] | ['Galvanised round steel wires'] | ['-30°C to +70°C'] | ['10 x cable diameter']
[16 empty] | 0.5 | 2 | 7/0.3 | 36 | 25 | 20 | 250 | 1 | 2000 | 2000
[16 empty] | 0.5 | 5 | 16/0.2 | 39 | 25 | 20 | 250 | 1 | 2000 | 2000
[16 empty] | 0.75 | 2 | 7/0.37 | 24.5 | 25 | 20 | 250 | 1 | 2000 | 2000
[16 empty] | 0.75 | 5 | 24/0.2 | 26 | 25 | 20 | 250 | 1 | 2000 | 2000
[16 empty] | 1 | 2 | 7/0.43 | 18.1 | 25 | 20 | 250 | 1 | 2000 | 2000
[16 empty] | 1 | 5 | 32/0.2 | 19.5 | 25 | 20 | 250 | 1 | 2000 | 2000
[16 empty] | 1.5 | 2 | 7/0.53 | 12.1 | 40 | 20 | 250 | 1 | 2000 | 2000
[16 empty] | 2.5 | 2 | 7/0.67 | 7.41 | 60 | 20 | 250 | 1 | 2000 | 2000
[26 empty] | Class 5 Conductor | 70550121050 |  |  |  | 11.1 | [8 empty] | 1 x 2 x 0.5 | 0.44 | 1 | 6.4 | 0.9 | 1.4 | 212.7
[26 empty] | Class 5 Conductor | 70550221050 |  |  |  | 12.4 | [8 empty] | 2 x 2 x 0.5 | 0.44 | 1 | 7.6 | 0.9 | 1.5 | 266.4
[26 empty] | Class 5 Conductor | 70550321050 |  |  |  | 13.7 | [8 empty] | 3 x 2 x 0.5 | 0.44 | 1 | 8.9 | 0.9 | 1.5 | 320.1
[26 empty] | Class 5 Conductor | 70550421050 |  |  |  | 14.7 | [8 empty] | 4 x 2 x 0.5 | 0.44 | 1 | 9.9 | 0.9 | 1.5 | 368.6
[26 empty] | Class 5 Conductor | 70550521050 |  |  |  | 15.7 | [8 empty] | 5 x 2 x 0.5 | 0.44 | 1 | 10.8 | 0.9 | 1.6 | 413.8
[26 empty] | Class 5 Conductor | 70550821050 |  |  |  | 18.1 | [8 empty] | 8 x 2 x 0.5 | 0.44 | 1 | 13.1 | 0.9 | 1.6 | 537.2
[26 empty] | Class 5 Conductor | 70551021050 |  |  |  | 19.5 | [8 empty] | 10 x 2 x 0.5 | 0.44 | 1 | 14.4 | 0.9 | 1.7 | 613.5
[26 empty] | Class 5 Conductor | 70551221050 |  |  |  | 21.4 | [8 empty] | 12 x 2 x 0.5 | 0.44 | 1 | 15.5 | 1.25 | 1.7 | 786.1
[26 empty] | Class 5 Conductor | 70551621050 |  |  |  | 23.6 | [8 empty] | 16 x 2 x 0.5 | 0.44 | 1 | 17.6 | 1.25 | 1.8 | 936.9
[26 empty] | Class 5 Conductor | 70552021050 |  |  |  | 25.5 | [8 empty] | 20 x 2 x 0.5 | 0.44 | 1 | 19.4 | 1.25 | 1.8 | 1080.4
[26 empty] | Class 5 Conductor | 70552421050 |  |  |  | 27.2 | [8 empty] | 24 x 2 x 0.5 | 0.44 | 1 | 21 | 1.25 | 1.9 | 1217.3
[26 empty] | Class 5 Conductor | 70550121075 |  |  |  | 11.5 | [8 empty] | 1 x 2 x 0.75 | 0.44 | 1 | 6.8 | 0.9 | 1.4 | 230
[26 empty] | Class 5 Conductor | 70550221075 |  |  |  | 12.9 | [8 empty] | 2 x 2 x 0.75 | 0.44 | 1 | 8.2 | 0.9 | 1.5 | 293.3
[26 empty] | Class 5 Conductor | 70550321075 |  |  |  | 14.3 | [8 empty] | 3 x 2 x 0.75 | 0.44 | 1 | 9.5 | 0.9 | 1.5 | 356.6
[26 empty] | Class 5 Conductor | 70550421075 |  |  |  | 15.5 | [8 empty] | 4 x 2 x 0.75 | 0.44 | 1 | 10.6 | 0.9 | 1.5 | 414.1
[26 empty] | Class 5 Conductor | 70550521075 |  |  |  | 16.6 | [8 empty] | 5 x 2 x 0.75 | 0.44 | 1 | 11.6 | 0.9 | 1.6 | 468
[26 empty] | Class 5 Conductor | 70550821075 |  |  |  | 19.2 | [8 empty] | 8 x 2 x 0.75 | 0.44 | 1 | 14.1 | 0.9 | 1.6 | 616.4
[26 empty] | Class 5 Conductor | 70551021075 |  |  |  | 21.4 | [8 empty] | 10 x 2 x 0.75 | 0.44 | 1 | 15.5 | 1.25 | 1.7 | 809.1
[26 empty] | Class 5 Conductor | 70551221075 |  |  |  | 22.8 | [8 empty] | 12 x 2 x 0.75 | 0.44 | 1 | 16.8 | 1.25 | 1.7 | 905.3
[26 empty] | Class 5 Conductor | 70551621075 |  |  |  | 25.1 | [8 empty] | 16 x 2 x 0.75 | 0.44 | 1 | 19 | 1.25 | 1.8 | 1088.2
[26 empty] | Class 5 Conductor | 70552021075 |  |  |  | 27.2 | [8 empty] | 20 x 2 x 0.75 | 0.44 | 1 | 21 | 1.25 | 1.9 | 1263.5
[26 empty] | Class 5 Conductor | 70552421075 |  |  |  | 29.1 | [8 empty] | 24 x 2 x 0.75 | 0.44 | 1 | 22.8 | 1.25 | 1.9 | 1431.3
[26 empty] | Class 5 Conductor | 70550120001 |  |  |  | 11.8 | [8 empty] | 1 x 2 x 1 | 0.44 | 1 | 7.1 | 0.9 | 1.4 | 244.2
[26 empty] | Class 5 Conductor | 70550220001 |  |  |  | 13.3 | [8 empty] | 2 x 2 x 1 | 0.44 | 1 | 8.5 | 0.9 | 1.5 | 315.6
[26 empty] | Class 5 Conductor | 70550320001 |  |  |  | 14.8 | [8 empty] | 3 x 2 x 1 | 0.44 | 1 | 10 | 0.9 | 1.5 | 387.2
[26 empty] | Class 5 Conductor | 70550420001 |  |  |  | 16.1 | [8 empty] | 4 x 2 x 1 | 0.44 | 1 | 11.2 | 0.9 | 1.6 | 452.6
[26 empty] | Class 5 Conductor | 70550520001 |  |  |  | 17.2 | [8 empty] | 5 x 2 x 1 | 0.44 | 1 | 12.2 | 0.9 | 1.6 | 514.2
[26 empty] | Class 5 Conductor | 70550820001 |  |  |  | 20 | [8 empty] | 8 x 2 x 1 | 0.44 | 1 | 14.9 | 0.9 | 1.7 | 684.7
[26 empty] | Class 5 Conductor | 70551020001 |  |  |  | 22.3 | [8 empty] | 10 x 2 x 1 | 0.44 | 1 | 16.4 | 1.25 | 1.7 | 897.2
[26 empty] | Class 5 Conductor | 70551220001 |  |  |  | 23.8 | [8 empty] | 12 x 2 x 1 | 0.44 | 1 | 17.7 | 1.25 | 1.8 | 1008.1
[26 empty] | Class 5 Conductor | 70551620001 |  |  |  | 26.3 | [8 empty] | 16 x 2 x 1 | 0.44 | 1 | 20.1 | 1.25 | 1.8 | 1219.5
[26 empty] | Class 5 Conductor | 70552020001 |  |  |  | 28.5 | [8 empty] | 20 x 2 x 1 | 0.44 | 1 | 22.3 | 1.25 | 1.9 | 1423.3
[26 empty] | Class 5 Conductor | 70552420001 |  |  |  | 30.6 | [8 empty] | 24 x 2 x 1 | 0.44 | 1 | 24.2 | 1.25 | 1.9 | 1618.8
[26 empty] | Class 2 Conductor | 70520121050 |  |  |  | 11.1 | [8 empty] | 1 x 2 x 0.5 | 0.44 | 1 | 6.4 | 0.9 | 1.4 | 212.5
[26 empty] | Class 2 Conductor | 70520221050 |  |  |  | 12.4 | [8 empty] | 2 x 2 x 0.5 | 0.44 | 1 | 7.6 | 0.9 | 1.5 | 266.1
[26 empty] | Class 2 Conductor | 70520321050 |  |  |  | 13.7 | [8 empty] | 3 x 2 x 0.5 | 0.44 | 1 | 8.9 | 0.9 | 1.5 | 319.7
[26 empty] | Class 2 Conductor | 70520421050 |  |  |  | 14.7 | [8 empty] | 4 x 2 x 0.5 | 0.44 | 1 | 9.9 | 0.9 | 1.5 | 368.1
[26 empty] | Class 2 Conductor | 70520521050 |  |  |  | 15.7 | [8 empty] | 5 x 2 x 0.5 | 0.44 | 1 | 10.8 | 0.9 | 1.6 | 413.1
[26 empty] | Class 2 Conductor | 70520821050 |  |  |  | 18.1 | [8 empty] | 8 x 2 x 0.5 | 0.44 | 1 | 13.1 | 0.9 | 1.6 | 536.2
[26 empty] | Class 2 Conductor | 70521021050 |  |  |  | 19.5 | [8 empty] | 10 x 2 x 0.5 | 0.44 | 1 | 14.4 | 0.9 | 1.7 | 612.2
[26 empty] | Class 2 Conductor | 70521221050 |  |  |  | 21.4 | [8 empty] | 12 x 2 x 0.5 | 0.44 | 1 | 15.5 | 1.25 | 1.7 | 784.6
[26 empty] | Class 2 Conductor | 70521621050 |  |  |  | 23.6 | [8 empty] | 16 x 2 x 0.5 | 0.44 | 1 | 17.6 | 1.25 | 1.8 | 934.9
[26 empty] | Class 2 Conductor | 70522021050 |  |  |  | 25.5 | [8 empty] | 20 x 2 x 0.5 | 0.44 | 1 | 19.4 | 1.25 | 1.8 | 1077.9
[26 empty] | Class 2 Conductor | 70522421050 |  |  |  | 27.2 | [8 empty] | 24 x 2 x 0.5 | 0.44 | 1 | 21 | 1.25 | 1.9 | 1214.3
[26 empty] | Class 2 Conductor | 70520121075 |  |  |  | 11.5 | [8 empty] | 1 x 2 x 0.75 | 0.44 | 1 | 6.8 | 0.9 | 1.4 | 230.4
[26 empty] | Class 2 Conductor | 70520221075 |  |  |  | 12.9 | [8 empty] | 2 x 2 x 0.75 | 0.44 | 1 | 8.2 | 0.9 | 1.5 | 293.7
[26 empty] | Class 2 Conductor | 70520321075 |  |  |  | 14.3 | [8 empty] | 3 x 2 x 0.75 | 0.44 | 1 | 9.5 | 0.9 | 1.5 | 357.1
[26 empty] | Class 2 Conductor | 70520421075 |  |  |  | 15.5 | [8 empty] | 4 x 2 x 0.75 | 0.44 | 1 | 10.6 | 0.9 | 1.5 | 414.8
[26 empty] | Class 2 Conductor | 70520521075 |  |  |  | 16.6 | [8 empty] | 5 x 2 x 0.75 | 0.44 | 1 | 11.6 | 0.9 | 1.6 | 468.8
[26 empty] | Class 2 Conductor | 70520821075 |  |  |  | 19.2 | [8 empty] | 8 x 2 x 0.75 | 0.44 | 1 | 14.1 | 0.9 | 1.6 | 617.4
[26 empty] | Class 2 Conductor | 70521021075 |  |  |  | 21.5 | [8 empty] | 10 x 2 x 0.75 | 0.44 | 1 | 15.6 | 1.25 | 1.7 | 810.5
[26 empty] | Class 2 Conductor | 70521221075 |  |  |  | 22.8 | [8 empty] | 12 x 2 x 0.75 | 0.44 | 1 | 16.8 | 1.25 | 1.7 | 906.9
[26 empty] | Class 2 Conductor | 70521621075 |  |  |  | 25.2 | [8 empty] | 16 x 2 x 0.75 | 0.44 | 1 | 19.1 | 1.25 | 1.8 | 1090
[26 empty] | Class 2 Conductor | 70522021075 |  |  |  | 27.3 | [8 empty] | 20 x 2 x 0.75 | 0.44 | 1 | 21.1 | 1.25 | 1.9 | 1265.6
[26 empty] | Class 2 Conductor | 70522421075 |  |  |  | 29.2 | [8 empty] | 24 x 2 x 0.75 | 0.44 | 1 | 22.9 | 1.25 | 1.9 | 1433.6
[26 empty] | Class 2 Conductor | 70520120001 |  |  |  | 11.7 | [8 empty] | 1 x 2 x 1 | 0.44 | 1 | 7.2 | 0.9 | 1.4 | 241.9
[26 empty] | Class 2 Conductor | 70520220001 |  |  |  | 13.5 | [8 empty] | 2 x 2 x 1 | 0.44 | 1 | 8.7 | 0.9 | 1.5 | 320.4
[26 empty] | Class 2 Conductor | 70520320001 |  |  |  | 15 | [8 empty] | 3 x 2 x 1 | 0.44 | 1 | 10.1 | 0.9 | 1.5 | 393.4
[26 empty] | Class 2 Conductor | 70520420001 |  |  |  | 16.3 | [8 empty] | 4 x 2 x 1 | 0.44 | 1 | 11.4 | 0.9 | 1.6 | 460.2
[26 empty] | Class 2 Conductor | 70520520001 |  |  |  | 17.4 | [8 empty] | 5 x 2 x 1 | 0.44 | 1 | 12.4 | 0.9 | 1.6 | 523
[26 empty] | Class 2 Conductor | 70520820001 |  |  |  | 21 | [8 empty] | 8 x 2 x 1 | 0.44 | 1 | 15.1 | 1.25 | 1.7 | 794.7
[26 empty] | Class 2 Conductor | 70521020001 |  |  |  | 22.6 | [8 empty] | 10 x 2 x 1 | 0.44 | 1 | 16.7 | 1.25 | 1.7 | 913.4
[26 empty] | Class 2 Conductor | 70521220001 |  |  |  | 24.1 | [8 empty] | 12 x 2 x 1 | 0.44 | 1 | 18.1 | 1.25 | 1.8 | 1026.4
[26 empty] | Class 2 Conductor | 70521620001 |  |  |  | 26.7 | [8 empty] | 16 x 2 x 1 | 0.44 | 1 | 20.5 | 1.25 | 1.8 | 1242.1
[26 empty] | Class 2 Conductor | 70522020001 |  |  |  | 29 | [8 empty] | 20 x 2 x 1 | 0.44 | 1 | 22.7 | 1.25 | 1.9 | 1449.9
[26 empty] | Class 2 Conductor | 70522420001 |  |  |  | 31 | [8 empty] | 24 x 2 x 1 | 0.44 | 1 | 24.6 | 1.25 | 2 | 1649.4
[26 empty] | Class 2 Conductor | 70520121105 |  |  |  | 12.6 | [8 empty] | 1 x 2 x 1.5 | 0.44 | 1 | 7.9 | 0.9 | 1.5 | 278.7
[26 empty] | Class 2 Conductor | 70520221105 |  |  |  | 14.4 | [8 empty] | 2 x 2 x 1.5 | 0.44 | 1 | 9.5 | 0.9 | 1.5 | 369.8
[26 empty] | Class 2 Conductor | 70520321105 |  |  |  | 16.1 | [8 empty] | 3 x 2 x 1.5 | 0.44 | 1 | 11.2 | 0.9 | 1.6 | 461.2
[26 empty] | Class 2 Conductor | 70520421105 |  |  |  | 17.6 | [8 empty] | 4 x 2 x 1.5 | 0.44 | 1 | 12.6 | 0.9 | 1.6 | 545.4
[26 empty] | Class 2 Conductor | 70520521105 |  |  |  | 18.9 | [8 empty] | 5 x 2 x 1.5 | 0.44 | 1 | 13.8 | 0.9 | 1.6 | 625.2
[26 empty] | Class 2 Conductor | 70520821105 |  |  |  | 22.8 | [8 empty] | 8 x 2 x 1.5 | 0.44 | 1 | 16.9 | 1.25 | 1.7 | 956.4
[26 empty] | Class 2 Conductor | 70521021105 |  |  |  | 24.7 | [8 empty] | 10 x 2 x 1.5 | 0.44 | 1 | 18.6 | 1.25 | 1.8 | 1108.5
[26 empty] | Class 2 Conductor | 70521221105 |  |  |  | 26.3 | [8 empty] | 12 x 2 x 1.5 | 0.44 | 1 | 20.1 | 1.25 | 1.8 | 1253.9
[26 empty] | Class 2 Conductor | 70521621105 |  |  |  | 29.2 | [8 empty] | 16 x 2 x 1.5 | 0.44 | 1 | 22.9 | 1.25 | 1.9 | 1532.9
[26 empty] | Class 2 Conductor | 70522021105 |  |  |  | 32.6 | [8 empty] | 20 x 2 x 1.5 | 0.44 | 1 | 25.4 | 1.6 | 2 | 1964.5
[26 empty] | Class 2 Conductor | 70522421105 |  |  |  | 35.3 | [8 empty] | 24 x 2 x 1.5 | 0.44 | 1.2 | 28 | 1.6 | 2.1 | 2282.1
[26 empty] | Class 2 Conductor | 70520121205 |  |  |  | 13.9 | [8 empty] | 1 x 2 x 2.5 | 0.53 | 1 | 9.1 | 0.9 | 1.5 | 338.1
[26 empty] | Class 2 Conductor | 70520221205 |  |  |  | 16.1 | [8 empty] | 2 x 2 x 2.5 | 0.53 | 1 | 11.1 | 0.9 | 1.6 | 464
[26 empty] | Class 2 Conductor | 70520321205 |  |  |  | 18.2 | [8 empty] | 3 x 2 x 2.5 | 0.53 | 1 | 13.1 | 0.9 | 1.6 | 590.4
[26 empty] | Class 2 Conductor | 70520421205 |  |  |  | 20 | [8 empty] | 4 x 2 x 2.5 | 0.53 | 1 | 14.8 | 0.9 | 1.7 | 708.2
[26 empty] | Class 2 Conductor | 70520521205 |  |  |  | 22.3 | [8 empty] | 5 x 2 x 2.5 | 0.53 | 1 | 16.3 | 1.25 | 1.7 | 925.5
[26 empty] | Class 2 Conductor | 70520821205 |  |  |  | 26.2 | [8 empty] | 8 x 2 x 2.5 | 0.53 | 1 | 20.1 | 1.25 | 1.8 | 1265.4
[26 empty] | Class 2 Conductor | 70521021205 |  |  |  | 28.4 | [8 empty] | 10 x 2 x 2.5 | 0.53 | 1 | 22.2 | 1.25 | 1.9 | 1481.4
[26 empty] | Class 2 Conductor | 70521221205 |  |  |  | 30.5 | [8 empty] | 12 x 2 x 2.5 | 0.53 | 1 | 24.1 | 1.25 | 1.9 | 1688.8
[26 empty] | Class 2 Conductor | 70521621205 |  |  |  | 35.2 | [8 empty] | 16 x 2 x 2.5 | 0.53 | 1.2 | 27.9 | 1.6 | 2.1 | 2306.2
[26 empty] | Class 2 Conductor | 70522021205 |  |  |  | 38.3 | [8 empty] | 20 x 2 x 2.5 | 0.53 | 1.2 | 30.8 | 1.6 | 2.2 | 2719.3
[26 empty] | Class 2 Conductor | 70522421205 |  |  |  | 41.2 | [8 empty] | 24 x 2 x 2.5 | 0.53 | 1.2 | 33.5 | 1.6 | 2.2 | 3117.3
https://www.rrkabel.com/instrumentation-cable/instrumentation-cable-re-ystysway-pimf-multi-pair | RE-Y(St)YSWAY PiMF – MULTI-PAIR | ['https://www.rrkabel.com/Uploads/Products/84/ProductZoomForMoreDetailsImage/02.jpg', 'https://www.rrkabel.com/Uploads/Products/84/ProductZoomImage/03.jpg', 'https://www.rrkabel.com/Uploads/Products/250/ProductFeaturesDetails/01.png', 'https://www.rrkabel.com/Uploads/Products/250/ProductFeaturesDetails/01.png'] | ['Adapted to EN 50288-7'] | ['Annealed copper wires according to BS EN 60228'] | ['Polyvinyl chloride PVC'] | ['Twisted'] | ['Black & white, continuously numbered on white core (1, 2, 3…) for multi-element'] |  | ['Aluminium / PETP tape over tinned copper drain wire'] | ['Polyvinyl chloride PVC'] | ['EN 60332-1-2'] | ['-30°C to +70°C Bending Radius: 10 x cable diameter'] |  | ['500V', '*Also available in 300V variant on request.'] | ['*For multi-pair maximum resistance shall be increased by 2%.'] | [17 empty] | ['Aluminium / PETP tape over tinned copper drain wire, plastic tape under and above screen'] | ['Concentric layers'] |  | ['Polyvinyl chloride PVC'] | ['Galvanised round steel wires']
[16 empty] | 0.5 | 2 | 7/0.3 | 36 | 25 | 20 | 250 | 1 | 2000 | 2000
[16 empty] | 0.5 | 5 | 16/0.2 | 39 | 25 | 20 | 250 | 1 | 2000 | 2000
[16 empty] | 0.75 | 2 | 7/0.37 | 24.5 | 25 | 20 | 250 | 1 | 2000 | 2000
[16 empty] | 0.75 | 5 | 24/0.2 | 26 | 25 | 20 | 250 | 1 | 2000 | 2000
[16 empty] | 1 | 2 | 7/0.43 | 18.1 | 25 | 20 | 250 | 1 | 2000 | 2000
[16 empty] | 1 | 5 | 32/0.2 | 19.5 | 25 | 20 | 250 | 1 | 2000 | 2000
[16 empty] | 1.5 | 2 | 7/0.53 | 12.1 | 40 | 20 | 250 | 1 | 2000 | 2000
[16 empty] | 2.5 | 2 | 7/0.67 | 7.41 | 60 | 20 | 250 | 1 | 2000 | 2000
[26 empty] | Class 5 Conductor | 70650221050 |  |  |  | 12.8 | 277.9 | [8 empty] | 0.44 | 1 | 8 |  | 1.5 |  | 2 x 2 x 0.5 | 0.9
[26 empty] | Class 5 Conductor | 70650321050 |  |  |  | 14.3 | 337.6 | [8 empty] | 0.44 | 1 | 9.5 |  | 1.5 |  | 3 x 2 x 0.5 | 0.9
[26 empty] | Class 5 Conductor | 70650421050 |  |  |  | 15.6 | 392.2 | [8 empty] | 0.44 | 1 | 10.7 |  | 1.5 |  | 4 x 2 x 0.5 | 0.9
[26 empty] | Class 5 Conductor | 70650521050 |  |  |  | 16.8 | 443.6 | [8 empty] | 0.44 | 1 | 11.8 |  | 1.6 |  | 5 x 2 x 0.5 | 0.9
[26 empty] | Class 5 Conductor | 70650821050 |  |  |  | 19.8 | 585.9 | [8 empty] | 0.44 | 1 | 14.7 |  | 1.7 |  | 8 x 2 x 0.5 | 0.9
[26 empty] | Class 5 Conductor | 70651021050 |  |  |  | 22.3 | 780.5 | [8 empty] | 0.44 | 1 | 16.4 |  | 1.7 |  | 10 x 2 x 0.5 | 1.25
[26 empty] | Class 5 Conductor | 70651221050 |  |  |  | 24 | 875.9 | [8 empty] | 0.44 | 1 | 17.9 |  | 1.8 |  | 12 x 2 x 0.5 | 1.25
[26 empty] | Class 5 Conductor | 70651621050 |  |  |  | 27 | 1058.7 | [8 empty] | 0.44 | 1 | 20.8 |  | 1.9 |  | 16 x 2 x 0.5 | 1.25
[26 empty] | Class 5 Conductor | 70652021050 |  |  |  | 29.7 | 1235.1 | [8 empty] | 0.44 | 1 | 23.4 |  | 1.9 |  | 20 x 2 x 0.5 | 1.25
[26 empty] | Class 5 Conductor | 70652421050 |  |  |  | 33.1 | 1569.3 | [8 empty] | 0.44 | 1 | 25.8 |  | 2 |  | 24 x 2 x 0.5 | 1.6
[26 empty] | Class 5 Conductor | 70650221075 |  |  |  | 13.3 | 304.8 | [8 empty] | 0.44 | 1 | 8.6 |  | 1.5 |  | 2 x 2 x 0.75 | 0.9
[26 empty] | Class 5 Conductor | 70650321075 |  |  |  | 15 | 374.2 | [8 empty] | 0.44 | 1 | 10.1 |  | 1.5 |  | 3 x 2 x 0.75 | 0.9
[26 empty] | Class 5 Conductor | 70650421075 |  |  |  | 16.4 | 437.9 | [8 empty] | 0.44 | 1 | 11.4 |  | 1.6 |  | 4 x 2 x 0.75 | 0.9
[26 empty] | Class 5 Conductor | 70650521075 |  |  |  | 17.6 | 498 | [8 empty] | 0.44 | 1 | 12.6 |  | 1.6 |  | 5 x 2 x 0.75 | 0.9
[26 empty] | Class 5 Conductor | 70650821075 |  |  |  | 21.6 | 766.9 | [8 empty] | 0.44 | 1 | 15.7 |  | 1.7 |  | 8 x 2 x 0.75 | 1.25
[26 empty] | Class 5 Conductor | 70651021075 |  |  |  | 23.5 | 883.8 | [8 empty] | 0.44 | 1 | 17.5 |  | 1.8 |  | 10 x 2 x 0.75 | 1.25
[26 empty] | Class 5 Conductor | 70651221075 |  |  |  | 25.3 | 995.9 | [8 empty] | 0.44 | 1 | 19.2 |  | 1.8 |  | 12 x 2 x 0.75 | 1.25
[26 empty] | Class 5 Conductor | 70651621075 |  |  |  | 28.5 | 1211.3 | [8 empty] | 0.44 | 1 | 22.2 |  | 1.9 |  | 16 x 2 x 0.75 | 1.25
[26 empty] | Class 5 Conductor | 70652021075 |  |  |  | 31.5 | 1420.1 | [8 empty] | 0.44 | 1 | 25 |  | 2 |  | 20 x 2 x 0.75 | 1.25
[26 empty] | Class 5 Conductor | 70652421075 |  |  |  | 35.4 | 1840.1 | [8 empty] | 0.44 | 1.2 | 28 |  | 2.1 |  | 24 x 2 x 0.75 | 1.6
[26 empty] | Class 5 Conductor | 70650220001 |  |  |  | 13.7 | 327.3 | [8 empty] | 0.44 | 1 | 8.9 |  | 1.5 |  | 2 x 2 x 1 | 0.9
[26 empty] | Class 5 Conductor | 70650320001 |  |  |  | 15.5 | 404.9 | [8 empty] | 0.44 | 1 | 10.6 |  | 1.5 |  | 3 x 2 x 1 | 0.9
[26 empty] | Class 5 Conductor | 70650420001 |  |  |  | 16.9 | 476.5 | [8 empty] | 0.44 | 1 | 12 |  | 1.6 |  | 4 x 2 x 1 | 0.9
[26 empty] | Class 5 Conductor | 70650520001 |  |  |  | 18.3 | 544.4 | [8 empty] | 0.44 | 1 | 13.2 |  | 1.6 |  | 5 x 2 x 1 | 0.9
[26 empty] | Class 5 Conductor | 70650820001 |  |  |  | 22.4 | 840.3 | [8 empty] | 0.44 | 1 | 16.5 |  | 1.7 |  | 8 x 2 x 1 | 1.25
[26 empty] | Class 5 Conductor | 70651020001 |  |  |  | 24.4 | 972.4 | [8 empty] | 0.44 | 1 | 18.4 |  | 1.8 |  | 10 x 2 x 1 | 1.25
[26 empty] | Class 5 Conductor | 70651220001 |  |  |  | 26.3 | 1099.3 | [8 empty] | 0.44 | 1 | 20.1 |  | 1.8 |  | 12 x 2 x 1 | 1.25
[26 empty] | Class 5 Conductor | 70651620001 |  |  |  | 29.7 | 1343.6 | [8 empty] | 0.44 | 1 | 23.3 |  | 1.9 |  | 16 x 2 x 1 | 1.25
[26 empty] | Class 5 Conductor | 70652020001 |  |  |  | 33.5 | 1747.4 | [8 empty] | 0.44 | 1 | 26.3 |  | 2 |  | 20 x 2 x 1 | 1.6
[26 empty] | Class 5 Conductor | 70652420001 |  |  |  | 36.8 | 2039 | [8 empty] | 0.44 | 1.2 | 29.4 |  | 2.1 |  | 24 x 2 x 1 | 1.6
[26 empty] | Class 2 Conductor | 70620221050 |  |  |  | 12.8 | 277.6 | [8 empty] | 0.44 | 1 | 8 |  | 1.5 |  | 2 x 2 x 0.5 | 0.9
[26 empty] | Class 2 Conductor | 70620321050 |  |  |  | 14.3 | 337.2 | [8 empty] | 0.44 | 1 | 9.5 |  | 1.5 |  | 3 x 2 x 0.5 | 0.9
[26 empty] | Class 2 Conductor | 70620421050 |  |  |  | 15.6 | 391.7 | [8 empty] | 0.44 | 1 | 10.7 |  | 1.5 |  | 4 x 2 x 0.5 | 0.9
[26 empty] | Class 2 Conductor | 70620521050 |  |  |  | 16.8 | 442.9 | [8 empty] | 0.44 | 1 | 11.8 |  | 1.6 |  | 5 x 2 x 0.5 | 0.9
[26 empty] | Class 2 Conductor | 70620821050 |  |  |  | 19.8 | 584.9 | [8 empty] | 0.44 | 1 | 14.7 |  | 1.7 |  | 8 x 2 x 0.5 | 0.9
[26 empty] | Class 2 Conductor | 70621021050 |  |  |  | 22.3 | 779.2 | [8 empty] | 0.44 | 1 | 16.4 |  | 1.7 |  | 10 x 2 x 0.5 | 1.25
[26 empty] | Class 2 Conductor | 70621221050 |  |  |  | 24 | 874.4 | [8 empty] | 0.44 | 1 | 17.9 |  | 1.8 |  | 12 x 2 x 0.5 | 1.25
[26 empty] | Class 2 Conductor | 70621621050 |  |  |  | 27 | 1056.7 | [8 empty] | 0.44 | 1 | 20.8 |  | 1.9 |  | 16 x 2 x 0.5 | 1.25
[26 empty] | Class 2 Conductor | 70622021050 |  |  |  | 29.7 | 1232.6 | [8 empty] | 0.44 | 1 | 23.4 |  | 1.9 |  | 20 x 2 x 0.5 | 1.25
[26 empty] | Class 2 Conductor | 70622421050 |  |  |  | 33.1 | 1566.3 | [8 empty] | 0.44 | 1 | 25.8 |  | 2 |  | 24 x 2 x 0.5 | 1.6
[26 empty] | Class 2 Conductor | 70620221075 |  |  |  | 13.4 | 305.3 | [8 empty] | 0.44 | 1 | 8.6 |  | 1.5 |  | 2 x 2 x 0.75 | 0.9
[26 empty] | Class 2 Conductor | 70620321075 |  |  |  | 15 | 374.7 | [8 empty] | 0.44 | 1 | 10.1 |  | 1.5 |  | 3 x 2 x 0.75 | 0.9
[26 empty] | Class 2 Conductor | 70620421075 |  |  |  | 16.4 | 438.5 | [8 empty] | 0.44 | 1 | 11.4 |  | 1.6 |  | 4 x 2 x 0.75 | 0.9
[26 empty] | Class 2 Conductor | 70620521075 |  |  |  | 17.7 | 498.8 | [8 empty] | 0.44 | 1 | 12.6 |  | 1.6 |  | 5 x 2 x 0.75 | 0.9
[26 empty] | Class 2 Conductor | 70620821075 |  |  |  | 21.7 | 768.1 | [8 empty] | 0.44 | 1 | 15.7 |  | 1.7 |  | 8 x 2 x 0.75 | 1.25
[26 empty] | Class 2 Conductor | 70621021075 |  |  |  | 23.6 | 885.2 | [8 empty] | 0.44 | 1 | 17.6 |  | 1.8 |  | 10 x 2 x 0.75 | 1.25
[26 empty] | Class 2 Conductor | 70621221075 |  |  |  | 25.3 | 997.5 | [8 empty] | 0.44 | 1 | 19.2 |  | 1.8 |  | 12 x 2 x 0.75 | 1.25
[26 empty] | Class 2 Conductor | 70621621075 |  |  |  | 28.6 | 1213.2 | [8 empty] | 0.44 | 1 | 22.3 |  | 1.9 |  | 16 x 2 x 0.75 | 1.25
[26 empty] | Class 2 Conductor | 70622021075 |  |  |  | 32.3 | 1581.2 | [8 empty] | 0.44 | 1 | 25.1 |  | 2 |  | 20 x 2 x 0.75 | 1.6
[26 empty] | Class 2 Conductor | 70622421075 |  |  |  | 35.4 | 1842.9 | [8 empty] | 0.44 | 1.2 | 28.1 |  | 2.1 |  | 24 x 2 x 0.75 | 1.6
[26 empty] | Class 2 Conductor | 70620220001 |  |  |  | 13.9 | 332 | [8 empty] | 0.44 | 1 | 9.1 |  | 1.5 |  | 2 x 2 x 1 | 0.9
[26 empty] | Class 2 Conductor | 70620320001 |  |  |  | 15.6 | 411.1 | [8 empty] | 0.44 | 1 | 10.7 |  | 1.6 |  | 3 x 2 x 1 | 0.9
[26 empty] | Class 2 Conductor | 70620420001 |  |  |  | 17.1 | 484.1 | [8 empty] | 0.44 | 1 | 12.2 |  | 1.6 |  | 4 x 2 x 1 | 0.9
[26 empty] | Class 2 Conductor | 70620520001 |  |  |  | 18.5 | 553.2 | [8 empty] | 0.44 | 1 | 13.4 |  | 1.6 |  | 5 x 2 x 1 | 0.9
[26 empty] | Class 2 Conductor | 70620820001 |  |  |  | 22.7 | 854.2 | [8 empty] | 0.44 | 1 | 16.7 |  | 1.7 |  | 8 x 2 x 1 | 1.25
[26 empty] | Class 2 Conductor | 70621020001 |  |  |  | 24.8 | 988.7 | [8 empty] | 0.44 | 1 | 18.7 |  | 1.8 |  | 10 x 2 x 1 | 1.25
[26 empty] | Class 2 Conductor | 70621220001 |  |  |  | 26.6 | 1117.8 | [8 empty] | 0.44 | 1 | 20.5 |  | 1.8 |  | 12 x 2 x 1 | 1.25
[26 empty] | Class 2 Conductor | 70621620001 |  |  |  | 30.1 | 1366.6 | [8 empty] | 0.44 | 1 | 23.7 |  | 1.9 |  | 16 x 2 x 1 | 1.25
[26 empty] | Class 2 Conductor | 70622020001 |  |  |  | 33.9 | 1777.1 | [8 empty] | 0.44 | 1 | 26.7 |  | 2 |  | 20 x 2 x 1 | 1.6
[26 empty] | Class 2 Conductor | 70622420001 |  |  |  | 37.3 | 2073.4 | [8 empty] | 0.44 | 1.2 | 29.8 |  | 2.1 |  | 24 x 2 x 1 | 1.6
[26 empty] | Class 2 Conductor | 70620221105 |  |  |  | 14.8 | 381.6 | [8 empty] | 0.44 | 1 | 9.9 |  | 1.5 |  | 2 x 2 x 1.5 | 0.9
[26 empty] | Class 2 Conductor | 70620321105 |  |  |  | 16.7 | 479 | [8 empty] | 0.44 | 1 | 11.8 |  | 1.6 |  | 3 x 2 x 1.5 | 0.9
[26 empty] | Class 2 Conductor | 70620421105 |  |  |  | 18.4 | 569.6 | [8 empty] | 0.44 | 1 | 13.4 |  | 1.6 |  | 4 x 2 x 1.5 | 0.9
[26 empty] | Class 2 Conductor | 70620521105 |  |  |  | 19.9 | 655.8 | [8 empty] | 0.44 | 1 | 14.8 |  | 1.7 |  | 5 x 2 x 1.5 | 0.9
[26 empty] | Class 2 Conductor | 70620821105 |  |  |  | 24.5 | 1016.7 | [8 empty] | 0.44 | 1 | 18.5 |  | 1.8 |  | 8 x 2 x 1.5 | 1.25
[26 empty] | Class 2 Conductor | 70621021105 |  |  |  | 26.8 | 1184.9 | [8 empty] | 0.44 | 1 | 20.6 |  | 1.8 |  | 10 x 2 x 1.5 | 1.25
[26 empty] | Class 2 Conductor | 70621221105 |  |  |  | 28.8 | 1346.7 | [8 empty] | 0.44 | 1 | 22.5 |  | 1.9 |  | 12 x 2 x 1.5 | 1.25
[26 empty] | Class 2 Conductor | 70621621105 |  |  |  | 33.4 | 1824.9 | [8 empty] | 0.44 | 1 | 26.1 |  | 2 |  | 16 x 2 x 1.5 | 1.6
[26 empty] | Class 2 Conductor | 70622021105 |  |  |  | 37.2 | 2195.6 | [8 empty] | 0.44 | 1.2 | 29.8 |  | 2.1 |  | 20 x 2 x 1.5 | 1.6
[26 empty] | Class 2 Conductor | 70622421105 |  |  |  | 40.4 | 2513.8 | [8 empty] | 0.44 | 1.2 | 32.8 |  | 2.2 |  | 24 x 2 x 1.5 | 1.6
[26 empty] | Class 2 Conductor | 70620221205 |  |  |  | 16.5 | 475.9 | [8 empty] | 0.53 | 1 | 11.5 |  | 1.6 |  | 2 x 2 x 2.5 | 0.9
[26 empty] | Class 2 Conductor | 70620321205 |  |  |  | 18.8 | 608.6 | [8 empty] | 0.53 | 1 | 13.7 |  | 1.6 |  | 3 x 2 x 2.5 | 0.9
[26 empty] | Class 2 Conductor | 70620421205 |  |  |  | 21.5 | 833.6 | [8 empty] | 0.53 | 1 | 15.6 |  | 1.7 |  | 4 x 2 x 2.5 | 1.25
[26 empty] | Class 2 Conductor | 70620521205 |  |  |  | 23.3 | 962.9 | [8 empty] | 0.53 | 1 | 17.3 |  | 1.8 |  | 5 x 2 x 2.5 | 1.25
[26 empty] | Class 2 Conductor | 70620821205 |  |  |  | 27.9 | 1327.1 | [8 empty] | 0.53 | 1 | 21.7 |  | 1.9 |  | 8 x 2 x 2.5 | 1.25
[26 empty] | Class 2 Conductor | 70621021205 |  |  |  | 30.6 | 1559.7 | [8 empty] | 0.53 | 1 | 24.2 |  | 1.9 |  | 10 x 2 x 2.5 | 1.25
[26 empty] | Class 2 Conductor | 70621221205 |  |  |  | 33.7 | 1951.8 | [8 empty] | 0.53 | 1 | 26.5 |  | 2 |  | 12 x 2 x 2.5 | 1.6
[26 empty] | Class 2 Conductor | 70621621205 |  |  |  | 38.6 | 2459.9 | [8 empty] | 0.53 | 1.2 | 31.1 |  | 2.2 |  | 16 x 2 x 2.5 | 1.6
[26 empty] | Class 2 Conductor | 70622021205 |  |  |  | 42.6 | 2915.1 | [8 empty] | 0.53 | 1.2 | 34.8 |  | 2.3 |  | 20 x 2 x 2.5 | 1.6
[26 empty] | Class 2 Conductor | 70622421205 |  |  |  | 47.1 | 3631.3 | [8 empty] | 0.53 | 1.2 | 38.3 |  | 2.4 |  | 24 x 2 x 2.5 | 2
https://www.rrkabel.com/instrumentation-cable/instrumentation-cable-re-2xstysway-single-multi-pair | RE-2X(St)YSWAY – SINGLE & MULTI-PAIR | ['https://www.rrkabel.com/Uploads/Products/85/ProductZoomForMoreDetailsImage/02.jpg', 'https://www.rrkabel.com/Uploads/Products/85/ProductZoomImage/03.jpg', 'https://www.rrkabel.com/Uploads/Products/253/ProductFeaturesDetails/01.png', 'https://www.rrkabel.com/Uploads/Products/253/ProductFeaturesDetails/01.png'] | ['Adapted to EN 50288-7'] | ['Annealed copper wires according to BS EN 60228'] | ['Crosslinked polyethylene XLPE'] | ['Twisted'] | ['Black & white, continuously numbered on white core (1, 2, 3…) for multi-element'] | ['1 layer of PETP tape'] | ['Aluminium / PETP tape over tinned copper drain wire'] | ['Polyvinyl chloride PVC (Also available in halogen free construction on request.)'] | ['EN 60332-1-2'] | ['-30°C to +90°C'] | ['10 x cable diameter'] | ['500V', '*Also available in 300V variant on request.'] | ['*For multi-pair maximum resistance shall be increased by 2%.'] | [20 empty] | ['Polyvinyl chloride PVC'] | ['Galvanised round steel wires']
[16 empty] | 0.5 | 2 | 7/0.3 | 36 | 25 | 5000 | 150 | 1 | 2000 | 2000
[16 empty] | 0.5 | 5 | 16/0.2 | 39 | 25 | 5000 | 150 | 1 | 2000 | 2000
[16 empty] | 0.75 | 2 | 7/0.37 | 24.5 | 25 | 5000 | 150 | 1 | 2000 | 2000
[16 empty] | 0.75 | 5 | 24/0.2 | 26 | 25 | 5000 | 150 | 1 | 2000 | 2000
[16 empty] | 1 | 2 | 7/0.43 | 18.1 | 25 | 5000 | 150 | 1 | 2000 | 2000
[16 empty] | 1 | 5 | 32/0.2 | 19.5 | 25 | 5000 | 150 | 1 | 2000 | 2000
[16 empty] | 1.5 | 2 | 7/0.53 | 12.1 | 40 | 5000 | 150 | 1 | 2000 | 2000
[16 empty] | 2.5 | 2 | 7/0.67 | 7.41 | 60 | 5000 | 150 | 1 | 2000 | 2000
[26 empty] | Class 5 Conductor | 70750121050 |  |  |  | 11.1 | 209.5 | [8 empty] | 0.44 | 1 | 6.4 |  | 1.4 |  | 1 x 2 x 0.5 | 0.9
[26 empty] | Class 5 Conductor | 70750221050 |  |  |  | 12.4 | 260.1 | [8 empty] | 0.44 | 1 | 7.6 |  | 1.5 |  | 2 x 2 x 0.5 | 0.9
[26 empty] | Class 5 Conductor | 70750321050 |  |  |  | 13.7 | 310.6 | [8 empty] | 0.44 | 1 | 8.9 |  | 1.5 |  | 3 x 2 x 0.5 | 0.9
[26 empty] | Class 5 Conductor | 70750421050 |  |  |  | 14.7 | 356 | [8 empty] | 0.44 | 1 | 9.9 |  | 1.5 |  | 4 x 2 x 0.5 | 0.9
[26 empty] | Class 5 Conductor | 70750521050 |  |  |  | 15.7 | 398 | [8 empty] | 0.44 | 1 | 10.8 |  | 1.6 |  | 5 x 2 x 0.5 | 0.9
[26 empty] | Class 5 Conductor | 70750821050 |  |  |  | 18.1 | 511.8 | [8 empty] | 0.44 | 1 | 13.1 |  | 1.6 |  | 8 x 2 x 0.5 | 0.9
[26 empty] | Class 5 Conductor | 70751021050 |  |  |  | 19.5 | 581.8 | [8 empty] | 0.44 | 1 | 14.4 |  | 1.7 |  | 10 x 2 x 0.5 | 0.9
[26 empty] | Class 5 Conductor | 70751221050 |  |  |  | 21.4 | 748.1 | [8 empty] | 0.44 | 1 | 15.5 |  | 1.7 |  | 12 x 2 x 0.5 | 1.25
[26 empty] | Class 5 Conductor | 70751621050 |  |  |  | 23.6 | 886.2 | [8 empty] | 0.44 | 1 | 17.6 |  | 1.8 |  | 16 x 2 x 0.5 | 1.25
[26 empty] | Class 5 Conductor | 70752021050 |  |  |  | 25.5 | 1017 | [8 empty] | 0.44 | 1 | 19.4 |  | 1.8 |  | 20 x 2 x 0.5 | 1.25
[26 empty] | Class 5 Conductor | 70752421050 |  |  |  | 27.2 | 1141.2 | [8 empty] | 0.44 | 1 | 21 |  | 1.9 |  | 24 x 2 x 0.5 | 1.25
[26 empty] | Class 5 Conductor | 70750121075 |  |  |  | 11.5 | 226.4 | [8 empty] | 0.44 | 1 | 6.8 |  | 1.4 |  | 1 x 2 x 0.75 | 0.9
[26 empty] | Class 5 Conductor | 70750221075 |  |  |  | 12.9 | 286 | [8 empty] | 0.44 | 1 | 8.2 |  | 1.5 |  | 2 x 2 x 0.75 | 0.9
[26 empty] | Class 5 Conductor | 70750321075 |  |  |  | 14.3 | 345.6 | [8 empty] | 0.44 | 1 | 9.5 |  | 1.5 |  | 3 x 2 x 0.75 | 0.9
[26 empty] | Class 5 Conductor | 70750421075 |  |  |  | 15.5 | 399.6 | [8 empty] | 0.44 | 1 | 10.6 |  | 1.5 |  | 4 x 2 x 0.75 | 0.9
[26 empty] | Class 5 Conductor | 70750521075 |  |  |  | 16.6 | 449.8 | [8 empty] | 0.44 | 1 | 11.6 |  | 1.6 |  | 5 x 2 x 0.75 | 0.9
[26 empty] | Class 5 Conductor | 70750821075 |  |  |  | 19.2 | 587.3 | [8 empty] | 0.44 | 1 | 14.1 |  | 1.6 |  | 8 x 2 x 0.75 | 0.9
[26 empty] | Class 5 Conductor | 70751021075 |  |  |  | 21.4 | 772.7 | [8 empty] | 0.44 | 1 | 15.5 |  | 1.7 |  | 10 x 2 x 0.75 | 1.25
[26 empty] | Class 5 Conductor | 70751221075 |  |  |  | 22.8 | 861.6 | [8 empty] | 0.44 | 1 | 16.8 |  | 1.7 |  | 12 x 2 x 0.75 | 1.25
[26 empty] | Class 5 Conductor | 70751621075 |  |  |  | 25.1 | 1030 | [8 empty] | 0.44 | 1 | 19 |  | 1.8 |  | 16 x 2 x 0.75 | 1.25
[26 empty] | Class 5 Conductor | 70752021075 |  |  |  | 27.2 | 1190.7 | [8 empty] | 0.44 | 1 | 21 |  | 1.9 |  | 20 x 2 x 0.75 | 1.25
[26 empty] | Class 5 Conductor | 70752421075 |  |  |  | 29.1 | 1344 | [8 empty] | 0.44 | 1 | 22.8 |  | 1.9 |  | 24 x 2 x 0.75 | 1.25
[26 empty] | Class 5 Conductor | 70750120001 |  |  |  | 11.8 | 240.2 | [8 empty] | 0.44 | 1 | 7.1 |  | 1.4 |  | 1 x 2 x 1 | 0.9
[26 empty] | Class 5 Conductor | 70750220001 |  |  |  | 13.3 | 307.7 | [8 empty] | 0.44 | 1 | 8.5 |  | 1.5 |  | 2 x 2 x 1 | 0.9
[26 empty] | Class 5 Conductor | 70750320001 |  |  |  | 14.8 | 375.3 | [8 empty] | 0.44 | 1 | 10 |  | 1.5 |  | 3 x 2 x 1 | 0.9
[26 empty] | Class 5 Conductor | 70750420001 |  |  |  | 16.1 | 436.8 | [8 empty] | 0.44 | 1 | 11.2 |  | 1.6 |  | 4 x 2 x 1 | 0.9
[26 empty] | Class 5 Conductor | 70750520001 |  |  |  | 17.2 | 494.4 | [8 empty] | 0.44 | 1 | 12.2 |  | 1.6 |  | 5 x 2 x 1 | 0.9
[26 empty] | Class 5 Conductor | 70750820001 |  |  |  | 20 | 653 | [8 empty] | 0.44 | 1 | 14.9 |  | 1.7 |  | 8 x 2 x 1 | 0.9
[26 empty] | Class 5 Conductor | 70751020001 |  |  |  | 22.3 | 857.5 | [8 empty] | 0.44 | 1 | 16.4 |  | 1.7 |  | 10 x 2 x 1 | 1.25
[26 empty] | Class 5 Conductor | 70751220001 |  |  |  | 23.8 | 960.4 | [8 empty] | 0.44 | 1 | 17.7 |  | 1.8 |  | 12 x 2 x 1 | 1.25
[26 empty] | Class 5 Conductor | 70751620001 |  |  |  | 26.3 | 1156 | [8 empty] | 0.44 | 1 | 20.1 |  | 1.8 |  | 16 x 2 x 1 | 1.25
[26 empty] | Class 5 Conductor | 70752020001 |  |  |  | 28.5 | 1343.9 | [8 empty] | 0.44 | 1 | 22.3 |  | 1.9 |  | 20 x 2 x 1 | 1.25
[26 empty] | Class 5 Conductor | 70752420001 |  |  |  | 30.6 | 1523.5 | [8 empty] | 0.44 | 1 | 24.2 |  | 1.9 |  | 24 x 2 x 1 | 1.25
[26 empty] | Class 2 Conductor | 70720121050 |  |  |  | 11.1 | 209.3 | [8 empty] | 0.44 | 1 | 6.4 |  | 1.4 |  | 1 x 2 x 0.5 | 0.9
[26 empty] | Class 2 Conductor | 70720221050 |  |  |  | 12.4 | 259.7 | [8 empty] | 0.44 | 1 | 7.6 |  | 1.5 |  | 2 x 2 x 0.5 | 0.9
[26 empty] | Class 2 Conductor | 70720321050 |  |  |  | 13.7 | 310.2 | [8 empty] | 0.44 | 1 | 8.9 |  | 1.5 |  | 3 x 2 x 0.5 | 0.9
[26 empty] | Class 2 Conductor | 70720421050 |  |  |  | 14.7 | 355.4 | [8 empty] | 0.44 | 1 | 9.9 |  | 1.5 |  | 4 x 2 x 0.5 | 0.9
[26 empty] | Class 2 Conductor | 70720521050 |  |  |  | 15.7 | 397.3 | [8 empty] | 0.44 | 1 | 10.8 |  | 1.6 |  | 5 x 2 x 0.5 | 0.9
[26 empty] | Class 2 Conductor | 70720821050 |  |  |  | 18.1 | 510.7 | [8 empty] | 0.44 | 1 | 13.1 |  | 1.6 |  | 8 x 2 x 0.5 | 0.9
[26 empty] | Class 2 Conductor | 70721021050 |  |  |  | 19.5 | 580.4 | [8 empty] | 0.44 | 1 | 14.4 |  | 1.7 |  | 10 x 2 x 0.5 | 0.9
[26 empty] | Class 2 Conductor | 70721221050 |  |  |  | 21.4 | 746.5 | [8 empty] | 0.44 | 1 | 15.5 |  | 1.7 |  | 12 x 2 x 0.5 | 1.25
[26 empty] | Class 2 Conductor | 70721621050 |  |  |  | 23.6 | 884 | [8 empty] | 0.44 | 1 | 17.6 |  | 1.8 |  | 16 x 2 x 0.5 | 1.25
[26 empty] | Class 2 Conductor | 70722021050 |  |  |  | 25.5 | 1014.3 | [8 empty] | 0.44 | 1 | 19.4 |  | 1.8 |  | 20 x 2 x 0.5 | 1.25
[26 empty] | Class 2 Conductor | 70722421050 |  |  |  | 27.2 | 1138 | [8 empty] | 0.44 | 1 | 21 |  | 1.9 |  | 24 x 2 x 0.5 | 1.25
[26 empty] | Class 2 Conductor | 70720121075 |  |  |  | 11.5 | 226.7 | [8 empty] | 0.44 | 1 | 6.8 |  | 1.4 |  | 1 x 2 x 0.75 | 0.9
[26 empty] | Class 2 Conductor | 70720221075 |  |  |  | 12.9 | 286.4 | [8 empty] | 0.44 | 1 | 8.2 |  | 1.5 |  | 2 x 2 x 0.75 | 0.9
[26 empty] | Class 2 Conductor | 70720321075 |  |  |  | 14.3 | 346.1 | [8 empty] | 0.44 | 1 | 9.5 |  | 1.5 |  | 3 x 2 x 0.75 | 0.9
[26 empty] | Class 2 Conductor | 70720421075 |  |  |  | 15.5 | 400.1 | [8 empty] | 0.44 | 1 | 10.6 |  | 1.5 |  | 4 x 2 x 0.75 | 0.9
[26 empty] | Class 2 Conductor | 70720521075 |  |  |  | 16.6 | 450.4 | [8 empty] | 0.44 | 1 | 11.6 |  | 1.6 |  | 5 x 2 x 0.75 | 0.9
[26 empty] | Class 2 Conductor | 70720821075 |  |  |  | 19.2 | 588 | [8 empty] | 0.44 | 1 | 14.1 |  | 1.6 |  | 8 x 2 x 0.75 | 0.9
[26 empty] | Class 2 Conductor | 70721021075 |  |  |  | 21.5 | 773.8 | [8 empty] | 0.44 | 1 | 15.6 |  | 1.7 |  | 10 x 2 x 0.75 | 1.25
[26 empty] | Class 2 Conductor | 70721221075 |  |  |  | 22.8 | 862.8 | [8 empty] | 0.44 | 1 | 16.8 |  | 1.7 |  | 12 x 2 x 0.75 | 1.25
[26 empty] | Class 2 Conductor | 70721621075 |  |  |  | 25.2 | 1031.2 | [8 empty] | 0.44 | 1 | 19.1 |  | 1.8 |  | 16 x 2 x 0.75 | 1.25
[26 empty] | Class 2 Conductor | 70722021075 |  |  |  | 27.3 | 1192.1 | [8 empty] | 0.44 | 1 | 21.1 |  | 1.9 |  | 20 x 2 x 0.75 | 1.25
[26 empty] | Class 2 Conductor | 70722421075 |  |  |  | 29.2 | 1345.5 | [8 empty] | 0.44 | 1 | 22.9 |  | 1.9 |  | 24 x 2 x 0.75 | 1.25
[26 empty] | Class 2 Conductor | 70720120001 |  |  |  | 11.7 | 237.9 | [8 empty] | 0.44 | 1 | 7.2 |  | 1.4 |  | 1 x 2 x 1 | 0.9
[26 empty] | Class 2 Conductor | 70720220001 |  |  |  | 13.5 | 312.5 | [8 empty] | 0.44 | 1 | 8.7 |  | 1.5 |  | 2 x 2 x 1 | 0.9
[26 empty] | Class 2 Conductor | 70720320001 |  |  |  | 15 | 381.6 | [8 empty] | 0.44 | 1 | 10.1 |  | 1.5 |  | 3 x 2 x 1 | 0.9
[26 empty] | Class 2 Conductor | 70720420001 |  |  |  | 16.3 | 444.5 | [8 empty] | 0.44 | 1 | 11.4 |  | 1.6 |  | 4 x 2 x 1 | 0.9
[26 empty] | Class 2 Conductor | 70720520001 |  |  |  | 17.4 | 503.3 | [8 empty] | 0.44 | 1 | 12.4 |  | 1.6 |  | 5 x 2 x 1 | 0.9
[26 empty] | Class 2 Conductor | 70720820001 |  |  |  | 21 | 763.3 | [8 empty] | 0.44 | 1 | 15.1 |  | 1.7 |  | 8 x 2 x 1 | 1.25
[26 empty] | Class 2 Conductor | 70721020001 |  |  |  | 22.6 | 874.1 | [8 empty] | 0.44 | 1 | 16.7 |  | 1.7 |  | 10 x 2 x 1 | 1.25
[26 empty] | Class 2 Conductor | 70721220001 |  |  |  | 24.1 | 979.3 | [8 empty] | 0.44 | 1 | 18.1 |  | 1.8 |  | 12 x 2 x 1 | 1.25
[26 empty] | Class 2 Conductor | 70721620001 |  |  |  | 26.7 | 1179.3 | [8 empty] | 0.44 | 1 | 20.5 |  | 1.8 |  | 16 x 2 x 1 | 1.25
[26 empty] | Class 2 Conductor | 70722020001 |  |  |  | 29 | 1371.4 | [8 empty] | 0.44 | 1 | 22.7 |  | 1.9 |  | 20 x 2 x 1 | 1.25
[26 empty] | Class 2 Conductor | 70722420001 |  |  |  | 31 | 1555.1 | [8 empty] | 0.44 | 1 | 24.6 |  | 2 |  | 24 x 2 x 1 | 1.25
[26 empty] | Class 2 Conductor | 70720121105 |  |  |  | 12.6 | 273.9 | [8 empty] | 0.44 | 1 | 7.9 |  | 1.5 |  | 1 x 2 x 1.5 | 0.9
[26 empty] | Class 2 Conductor | 70720221105 |  |  |  | 14.4 | 360.3 | [8 empty] | 0.44 | 1 | 9.5 |  | 1.5 |  | 2 x 2 x 1.5 | 0.9
[26 empty] | Class 2 Conductor | 70720321105 |  |  |  | 16.1 | 446.8 | [8 empty] | 0.44 | 1 | 11.2 |  | 1.6 |  | 3 x 2 x 1.5 | 0.9
[26 empty] | Class 2 Conductor | 70720421105 |  |  |  | 17.6 | 526.3 | [8 empty] | 0.44 | 1 | 12.6 |  | 1.6 |  | 4 x 2 x 1.5 | 0.9
[26 empty] | Class 2 Conductor | 70720521105 |  |  |  | 18.9 | 601.2 | [8 empty] | 0.44 | 1 | 13.8 |  | 1.6 |  | 5 x 2 x 1.5 | 0.9
[26 empty] | Class 2 Conductor | 70720821105 |  |  |  | 22.8 | 918.1 | [8 empty] | 0.44 | 1 | 16.9 |  | 1.7 |  | 8 x 2 x 1.5 | 1.25
[26 empty] | Class 2 Conductor | 70721021105 |  |  |  | 24.7 | 1060.6 | [8 empty] | 0.44 | 1 | 18.6 |  | 1.8 |  | 10 x 2 x 1.5 | 1.25
[26 empty] | Class 2 Conductor | 70721221105 |  |  |  | 26.3 | 1196.4 | [8 empty] | 0.44 | 1 | 20.1 |  | 1.8 |  | 12 x 2 x 1.5 | 1.25
[26 empty] | Class 2 Conductor | 70721621105 |  |  |  | 29.2 | 1456.3 | [8 empty] | 0.44 | 1 | 22.9 |  | 1.9 |  | 16 x 2 x 1.5 | 1.25
[26 empty] | Class 2 Conductor | 70722021105 |  |  |  | 32.6 | 1868.7 | [8 empty] | 0.44 | 1 | 25.4 |  | 2 |  | 20 x 2 x 1.5 | 1.6
[26 empty] | Class 2 Conductor | 70722421105 |  |  |  | 35.3 | 2167.1 | [8 empty] | 0.44 | 1.2 | 28 |  | 2.1 |  | 24 x 2 x 1.5 | 1.6
[26 empty] | Class 2 Conductor | 70720121205 |  |  |  | 13.9 | 331.1 | [8 empty] | 0.53 | 1 | 9.1 |  | 1.5 |  | 1 x 2 x 2.5 | 0.9
[26 empty] | Class 2 Conductor | 70720221205 |  |  |  | 16.1 | 450.1 | [8 empty] | 0.53 | 1 | 11.1 |  | 1.6 |  | 2 x 2 x 2.5 | 0.9
[26 empty] | Class 2 Conductor | 70720321205 |  |  |  | 18.2 | 569.5 | [8 empty] | 0.53 | 1 | 13.1 |  | 1.6 |  | 3 x 2 x 2.5 | 0.9
[26 empty] | Class 2 Conductor | 70720421205 |  |  |  | 20 | 680.4 | [8 empty] | 0.53 | 1 | 14.8 |  | 1.7 |  | 4 x 2 x 2.5 | 0.9
[26 empty] | Class 2 Conductor | 70720521205 |  |  |  | 22.3 | 890.7 | [8 empty] | 0.53 | 1 | 16.3 |  | 1.7 |  | 5 x 2 x 2.5 | 1.25
[26 empty] | Class 2 Conductor | 70720821205 |  |  |  | 26.2 | 1209.8 | [8 empty] | 0.53 | 1 | 20.1 |  | 1.8 |  | 8 x 2 x 2.5 | 1.25
[26 empty] | Class 2 Conductor | 70721021205 |  |  |  | 28.4 | 1411.9 | [8 empty] | 0.53 | 1 | 22.2 |  | 1.9 |  | 10 x 2 x 2.5 | 1.25
[26 empty] | Class 2 Conductor | 70721221205 |  |  |  | 30.5 | 1605.5 | [8 empty] | 0.53 | 1 | 24.1 |  | 1.9 |  | 12 x 2 x 2.5 | 1.25
[26 empty] | Class 2 Conductor | 70721621205 |  |  |  | 35.2 | 2195.1 | [8 empty] | 0.53 | 1.2 | 27.9 |  | 2.1 |  | 16 x 2 x 2.5 | 1.6
[26 empty] | Class 2 Conductor | 70722021205 |  |  |  | 38.3 | 2580.4 | [8 empty] | 0.53 | 1.2 | 30.8 |  | 2.2 |  | 20 x 2 x 2.5 | 1.6
[26 empty] | Class 2 Conductor | 70722421205 |  |  |  | 41.2 | 2950.5 | [8 empty] | 0.53 | 1.2 | 33.5 |  | 2.2 |  | 24 x 2 x 2.5 | 1.6
https://www.rrkabel.com/instrumentation-cable/instrumentation-cable-re-2xstysway-pimf-multi-pair | RE-2X(St)YSWAY PiMF – MULTI-PAIR | ['https://www.rrkabel.com/Uploads/Products/86/ProductZoomForMoreDetailsImage/02.jpg', 'https://www.rrkabel.com/Uploads/Products/86/ProductZoomImage/03.jpg', 'https://www.rrkabel.com/Uploads/Products/256/ProductFeaturesDetails/01.png', 'https://www.rrkabel.com/Uploads/Products/256/ProductFeaturesDetails/01.png'] | ['Adapted to EN 50288-7'] | [45 empty] | ['Annealed copper wires according to BS EN 60228'] | ['Crosslinked polyethylene XLPE'] | ['Twisted'] | ['Black & white, continuously numbered on white core (1, 2, 3…) for multi-element'] | ['Aluminium / PETP tape over tinned copper drain wire, plastic tape under and above screen'] | ['Concentric layers'] | ['Aluminium / PETP tape over tinned copper drain wire'] | ['Polyvinyl chloride PVC'] | ['Galvanised round steel wires'] | ['Polyvinyl chloride PVC (Also available in halogen free construction, on request.)'] | ['EN 60332-1-2'] | ['-30°C to +90°C'] | ['10 x cable diameter'] | ['500V', '*Also available in 300V variant on request.']
[16 empty] | 0.5 | 2 | 7/0.3 | 36.7 | 25 | 5000 | 150 | 1 | 2000 | 2000
[16 empty] | 0.5 | 5 | 16/0.2 | 39.8 | 25 | 5000 | 150 | 1 | 2000 | 2000
[16 empty] | 0.75 | 2 | 7/0.37 | 25 | 25 | 5000 | 150 | 1 | 2000 | 2000
[16 empty] | 0.75 | 5 | 24/0.2 | 26.5 | 25 | 5000 | 150 | 1 | 2000 | 2000
[16 empty] | 1 | 2 | 7/0.43 | 18.5 | 25 | 5000 | 150 | 1 | 2000 | 2000
[16 empty] | 1 | 5 | 32/0.2 | 19.9 | 25 | 5000 | 150 | 1 | 2000 | 2000
[16 empty] | 1.5 | 2 | 7/0.53 | 12.3 | 40 | 5000 | 150 | 1 | 2000 | 2000
[16 empty] | 2.5 | 2 | 7/0.67 | 7.6 | 60 | 5000 | 150 | 1 | 2000 | 2000
[26 empty] | Class 5 Conductor | 70850221050 |  |  |  | 12.8 | [8 empty] | 2 x 2 x 0.5 | 0.44 | 1 | 8 | 0.9 | 1.5 | 271.6
[26 empty] | Class 5 Conductor | 70850321050 |  |  |  | 14.3 | [8 empty] | 3 x 2 x 0.5 | 0.44 | 1 | 9.5 | 0.9 | 1.5 | 328.1
[26 empty] | Class 5 Conductor | 70850421050 |  |  |  | 15.6 | [8 empty] | 4 x 2 x 0.5 | 0.44 | 1 | 10.7 | 0.9 | 1.5 | 379.6
[26 empty] | Class 5 Conductor | 70850521050 |  |  |  | 16.8 | [8 empty] | 5 x 2 x 0.5 | 0.44 | 1 | 11.8 | 0.9 | 1.6 | 427.7
[26 empty] | Class 5 Conductor | 70850821050 |  |  |  | 19.8 | [8 empty] | 8 x 2 x 0.5 | 0.44 | 1 | 14.7 | 0.9 | 1.7 | 560.6
[26 empty] | Class 5 Conductor | 70851021050 |  |  |  | 22.3 | [8 empty] | 10 x 2 x 0.5 | 0.44 | 1 | 16.4 | 1.25 | 1.7 | 748.8
[26 empty] | Class 5 Conductor | 70851221050 |  |  |  | 24 | [8 empty] | 12 x 2 x 0.5 | 0.44 | 1 | 17.9 | 1.25 | 1.8 | 837.9
[26 empty] | Class 5 Conductor | 70851621050 |  |  |  | 27 | [8 empty] | 16 x 2 x 0.5 | 0.44 | 1 | 20.8 | 1.25 | 1.9 | 1008
[26 empty] | Class 5 Conductor | 70852021050 |  |  |  | 29.7 | [8 empty] | 20 x 2 x 0.5 | 0.44 | 1 | 23.4 | 1.25 | 1.9 | 1171.7
[26 empty] | Class 5 Conductor | 70852421050 |  |  |  | 33.1 | [8 empty] | 24 x 2 x 0.5 | 0.44 | 1 | 25.8 | 1.6 | 2 | 1493.2
[26 empty] | Class 5 Conductor | 70850221075 |  |  |  | 13.3 | [8 empty] | 2 x 2 x 0.75 | 0.44 | 1 | 8.6 | 0.9 | 1.5 | 297.6
[26 empty] | Class 5 Conductor | 70850321075 |  |  |  | 15 | [8 empty] | 3 x 2 x 0.75 | 0.44 | 1 | 10.1 | 0.9 | 1.5 | 363.2
[26 empty] | Class 5 Conductor | 70850421075 |  |  |  | 16.4 | [8 empty] | 4 x 2 x 0.75 | 0.44 | 1 | 11.4 | 0.9 | 1.6 | 423.3
[26 empty] | Class 5 Conductor | 70850521075 |  |  |  | 17.6 | [8 empty] | 5 x 2 x 0.75 | 0.44 | 1 | 12.6 | 0.9 | 1.6 | 479.8
[26 empty] | Class 5 Conductor | 70850821075 |  |  |  | 21.6 | [8 empty] | 8 x 2 x 0.75 | 0.44 | 1 | 15.7 | 1.25 | 1.7 | 737.8
[26 empty] | Class 5 Conductor | 70851021075 |  |  |  | 23.5 | [8 empty] | 10 x 2 x 0.75 | 0.44 | 1 | 17.5 | 1.25 | 1.8 | 847.4
[26 empty] | Class 5 Conductor | 70851221075 |  |  |  | 25.3 | [8 empty] | 12 x 2 x 0.75 | 0.44 | 1 | 19.2 | 1.25 | 1.8 | 952.2
[26 empty] | Class 5 Conductor | 70851621075 |  |  |  | 28.5 | [8 empty] | 16 x 2 x 0.75 | 0.44 | 1 | 22.2 | 1.25 | 1.9 | 1153.1
[26 empty] | Class 5 Conductor | 70852021075 |  |  |  | 31.5 | [8 empty] | 20 x 2 x 0.75 | 0.44 | 1 | 25 | 1.25 | 2 | 1347.3
[26 empty] | Class 5 Conductor | 70852421075 |  |  |  | 35.4 | [8 empty] | 24 x 2 x 0.75 | 0.44 | 1.2 | 28 | 1.6 | 2.1 | 1752.7
[26 empty] | Class 5 Conductor | 70850220001 |  |  |  | 13.7 | [8 empty] | 2 x 2 x 1 | 0.44 | 1 | 8.9 | 0.9 | 1.5 | 319.3
[26 empty] | Class 5 Conductor | 70850320001 |  |  |  | 15.5 | [8 empty] | 3 x 2 x 1 | 0.44 | 1 | 10.6 | 0.9 | 1.5 | 393
[26 empty] | Class 5 Conductor | 70850420001 |  |  |  | 16.9 | [8 empty] | 4 x 2 x 1 | 0.44 | 1 | 12 | 0.9 | 1.6 | 460.6
[26 empty] | Class 5 Conductor | 70850520001 |  |  |  | 18.3 | [8 empty] | 5 x 2 x 1 | 0.44 | 1 | 13.2 | 0.9 | 1.6 | 524.5
[26 empty] | Class 5 Conductor | 70850820001 |  |  |  | 22.4 | [8 empty] | 8 x 2 x 1 | 0.44 | 1 | 16.5 | 1.25 | 1.7 | 808.5
[26 empty] | Class 5 Conductor | 70851020001 |  |  |  | 24.4 | [8 empty] | 10 x 2 x 1 | 0.44 | 1 | 18.4 | 1.25 | 1.8 | 932.7
[26 empty] | Class 5 Conductor | 70851220001 |  |  |  | 26.3 | [8 empty] | 12 x 2 x 1 | 0.44 | 1 | 20.1 | 1.25 | 1.8 | 1051.6
[26 empty] | Class 5 Conductor | 70851620001 |  |  |  | 29.7 | [8 empty] | 16 x 2 x 1 | 0.44 | 1 | 23.3 | 1.25 | 1.9 | 1280.1
[26 empty] | Class 5 Conductor | 70852020001 |  |  |  | 33.5 | [8 empty] | 20 x 2 x 1 | 0.44 | 1 | 26.3 | 1.6 | 2 | 1668
[26 empty] | Class 5 Conductor | 70852420001 |  |  |  | 36.8 | [8 empty] | 24 x 2 x 1 | 0.44 | 1.2 | 29.4 | 1.6 | 2.1 | 1943.7
[26 empty] | Class 2 Conductor | 70820221050 |  |  |  | 12.8 | [8 empty] | 2 x 2 x 0.5 | 0.44 | 1 | 8 | 0.9 | 1.5 | 271.3
[26 empty] | Class 2 Conductor | 70820321050 |  |  |  | 14.3 | [8 empty] | 3 x 2 x 0.5 | 0.44 | 1 | 9.5 | 0.9 | 1.5 | 327.7
[26 empty] | Class 2 Conductor | 70820421050 |  |  |  | 15.6 | [8 empty] | 4 x 2 x 0.5 | 0.44 | 1 | 10.7 | 0.9 | 1.5 | 379
[26 empty] | Class 2 Conductor | 70820521050 |  |  |  | 16.8 | [8 empty] | 5 x 2 x 0.5 | 0.44 | 1 | 11.8 | 0.9 | 1.6 | 427
[26 empty] | Class 2 Conductor | 70820821050 |  |  |  | 19.8 | [8 empty] | 8 x 2 x 0.5 | 0.44 | 1 | 14.7 | 0.9 | 1.7 | 559.5
[26 empty] | Class 2 Conductor | 70821021050 |  |  |  | 22.3 | [8 empty] | 10 x 2 x 0.5 | 0.44 | 1 | 16.4 | 1.25 | 1.7 | 747.4
[26 empty] | Class 2 Conductor | 70821221050 |  |  |  | 24 | [8 empty] | 12 x 2 x 0.5 | 0.44 | 1 | 17.9 | 1.25 | 1.8 | 836.3
[26 empty] | Class 2 Conductor | 70821621050 |  |  |  | 27 | [8 empty] | 16 x 2 x 0.5 | 0.44 | 1 | 20.8 | 1.25 | 1.9 | 1005.9
[26 empty] | Class 2 Conductor | 70822021050 |  |  |  | 29.7 | [8 empty] | 20 x 2 x 0.5 | 0.44 | 1 | 23.4 | 1.25 | 1.9 | 1169.1
[26 empty] | Class 2 Conductor | 70822421050 |  |  |  | 33.1 | [8 empty] | 24 x 2 x 0.5 | 0.44 | 1 | 25.8 | 1.6 | 2 | 1490.1
[26 empty] | Class 2 Conductor | 70820221075 |  |  |  | 13.4 | [8 empty] | 2 x 2 x 0.75 | 0.44 | 1 | 8.6 | 0.9 | 1.5 | 297.9
[26 empty] | Class 2 Conductor | 70820321075 |  |  |  | 15 | [8 empty] | 3 x 2 x 0.75 | 0.44 | 1 | 10.1 | 0.9 | 1.5 | 363.7
[26 empty] | Class 2 Conductor | 70820421075 |  |  |  | 16.4 | [8 empty] | 4 x 2 x 0.75 | 0.44 | 1 | 11.4 | 0.9 | 1.6 | 423.8
[26 empty] | Class 2 Conductor | 70820521075 |  |  |  | 17.7 | [8 empty] | 5 x 2 x 0.75 | 0.44 | 1 | 12.6 | 0.9 | 1.6 | 480.4
[26 empty] | Class 2 Conductor | 70820821075 |  |  |  | 21.7 | [8 empty] | 8 x 2 x 0.75 | 0.44 | 1 | 15.7 | 1.25 | 1.7 | 738.7
[26 empty] | Class 2 Conductor | 70821021075 |  |  |  | 23.6 | [8 empty] | 10 x 2 x 0.75 | 0.44 | 1 | 17.6 | 1.25 | 1.8 | 848.5
[26 empty] | Class 2 Conductor | 70821221075 |  |  |  | 25.3 | [8 empty] | 12 x 2 x 0.75 | 0.44 | 1 | 19.2 | 1.25 | 1.8 | 953.4
[26 empty] | Class 2 Conductor | 70821621075 |  |  |  | 28.6 | [8 empty] | 16 x 2 x 0.75 | 0.44 | 1 | 22.3 | 1.25 | 1.9 | 1154.4
[26 empty] | Class 2 Conductor | 70822021075 |  |  |  | 32.3 | [8 empty] | 20 x 2 x 0.75 | 0.44 | 1 | 25.1 | 1.6 | 2 | 1507.7
[26 empty] | Class 2 Conductor | 70822421075 |  |  |  | 35.4 | [8 empty] | 24 x 2 x 0.75 | 0.44 | 1.2 | 28.1 | 1.6 | 2.1 | 1754.7
[26 empty] | Class 2 Conductor | 70820220001 |  |  |  | 13.9 | [8 empty] | 2 x 2 x 1 | 0.44 | 1 | 9.1 | 0.9 | 1.5 | 324.2
[26 empty] | Class 2 Conductor | 70820320001 |  |  |  | 15.6 | [8 empty] | 3 x 2 x 1 | 0.44 | 1 | 10.7 | 0.9 | 1.6 | 399.3
[26 empty] | Class 2 Conductor | 70820420001 |  |  |  | 17.1 | [8 empty] | 4 x 2 x 1 | 0.44 | 1 | 12.2 | 0.9 | 1.6 | 468.4
[26 empty] | Class 2 Conductor | 70820520001 |  |  |  | 18.5 | [8 empty] | 5 x 2 x 1 | 0.44 | 1 | 13.4 | 0.9 | 1.6 | 533.5
[26 empty] | Class 2 Conductor | 70820820001 |  |  |  | 22.7 | [8 empty] | 8 x 2 x 1 | 0.44 | 1 | 16.7 | 1.25 | 1.7 | 822.8
[26 empty] | Class 2 Conductor | 70821020001 |  |  |  | 24.8 | [8 empty] | 10 x 2 x 1 | 0.44 | 1 | 18.7 | 1.25 | 1.8 | 949.4
[26 empty] | Class 2 Conductor | 70821220001 |  |  |  | 26.6 | [8 empty] | 12 x 2 x 1 | 0.44 | 1 | 20.5 | 1.25 | 1.8 | 1070.7
[26 empty] | Class 2 Conductor | 70821620001 |  |  |  | 30.1 | [8 empty] | 16 x 2 x 1 | 0.44 | 1 | 23.7 | 1.25 | 1.9 | 1303.7
[26 empty] | Class 2 Conductor | 70822020001 |  |  |  | 33.9 | [8 empty] | 20 x 2 x 1 | 0.44 | 1 | 26.7 | 1.6 | 2 | 1698.5
[26 empty] | Class 2 Conductor | 70822420001 |  |  |  | 37.3 | [8 empty] | 24 x 2 x 1 | 0.44 | 1.2 | 29.8 | 1.6 | 2.1 | 1979.1
[26 empty] | Class 2 Conductor | 70820221105 |  |  |  | 14.8 | [8 empty] | 2 x 2 x 1.5 | 0.44 | 1 | 9.9 | 0.9 | 1.5 | 372
[26 empty] | Class 2 Conductor | 70820321105 |  |  |  | 16.7 | [8 empty] | 3 x 2 x 1.5 | 0.44 | 1 | 11.8 | 0.9 | 1.6 | 464.7
[26 empty] | Class 2 Conductor | 70820421105 |  |  |  | 18.4 | [8 empty] | 4 x 2 x 1.5 | 0.44 | 1 | 13.4 | 0.9 | 1.6 | 550.4
[26 empty] | Class 2 Conductor | 70820521105 |  |  |  | 19.9 | [8 empty] | 5 x 2 x 1.5 | 0.44 | 1 | 14.8 | 0.9 | 1.7 | 631.8
[26 empty] | Class 2 Conductor | 70820821105 |  |  |  | 24.5 | [8 empty] | 8 x 2 x 1.5 | 0.44 | 1 | 18.5 | 1.25 | 1.8 | 978.4
[26 empty] | Class 2 Conductor | 70821021105 |  |  |  | 26.8 | [8 empty] | 10 x 2 x 1.5 | 0.44 | 1 | 20.6 | 1.25 | 1.8 | 1136.9
[26 empty] | Class 2 Conductor | 70821221105 |  |  |  | 28.8 | [8 empty] | 12 x 2 x 1.5 | 0.44 | 1 | 22.5 | 1.25 | 1.9 | 1289.2
[26 empty] | Class 2 Conductor | 70821621105 |  |  |  | 33.4 | [8 empty] | 16 x 2 x 1.5 | 0.44 | 1 | 26.1 | 1.6 | 2 | 1748.2
[26 empty] | Class 2 Conductor | 70822021105 |  |  |  | 37.2 | [8 empty] | 20 x 2 x 1.5 | 0.44 | 1.2 | 29.8 | 1.6 | 2.1 | 2099.8
[26 empty] | Class 2 Conductor | 70822421105 |  |  |  | 40.4 | [8 empty] | 24 x 2 x 1.5 | 0.44 | 1.2 | 32.8 | 1.6 | 2.2 | 2398.8
[26 empty] | Class 2 Conductor | 70820221205 |  |  |  | 16.5 | [8 empty] | 2 x 2 x 2.5 | 0.53 | 1 | 11.5 | 0.9 | 1.6 | 462
[26 empty] | Class 2 Conductor | 70820321205 |  |  |  | 18.8 | [8 empty] | 3 x 2 x 2.5 | 0.53 | 1 | 13.7 | 0.9 | 1.6 | 587.8
[26 empty] | Class 2 Conductor | 70820421205 |  |  |  | 21.5 | [8 empty] | 4 x 2 x 2.5 | 0.53 | 1 | 15.6 | 1.25 | 1.7 | 805.8
[26 empty] | Class 2 Conductor | 70820521205 |  |  |  | 23.3 | [8 empty] | 5 x 2 x 2.5 | 0.53 | 1 | 17.3 | 1.25 | 1.8 | 928.2
[26 empty] | Class 2 Conductor | 70820821205 |  |  |  | 27.9 | [8 empty] | 8 x 2 x 2.5 | 0.53 | 1 | 21.7 | 1.25 | 1.9 | 1271.5
[26 empty] | Class 2 Conductor | 70821021205 |  |  |  | 30.6 | [8 empty] | 10 x 2 x 2.5 | 0.53 | 1 | 24.2 | 1.25 | 1.9 | 1490.3
[26 empty] | Class 2 Conductor | 70821221205 |  |  |  | 33.7 | [8 empty] | 12 x 2 x 2.5 | 0.53 | 1 | 26.5 | 1.6 | 2 | 1868.5
[26 empty] | Class 2 Conductor | 70821621205 |  |  |  | 38.6 | [8 empty] | 16 x 2 x 2.5 | 0.53 | 1.2 | 31.1 | 1.6 | 2.2 | 2348.7
[26 empty] | Class 2 Conductor | 70822021205 |  |  |  | 42.6 | [8 empty] | 20 x 2 x 2.5 | 0.53 | 1.2 | 34.8 | 1.6 | 2.3 | 2776.2
[26 empty] | Class 2 Conductor | 70822421205 |  |  |  | 47.1 | [8 empty] | 24 x 2 x 2.5 | 0.53 | 1.2 | 38.3 | 2 | 2.4 | 3464.6
https://www.rrkabel.com/instrumentation-cable/instrumentation-cable-re-ysty-multicore | RE-Y(St)Y – MULTICORE | ['https://www.rrkabel.com/Uploads/Products/87/ProductZoomForMoreDetailsImage/02.jpg', 'https://www.rrkabel.com/Uploads/Products/87/ProductZoomImage/03.jpg', 'https://www.rrkabel.com/Uploads/Products/259/ProductFeaturesDetails/01.png', 'https://www.rrkabel.com/Uploads/Products/259/ProductFeaturesDetails/01.png'] | ['Adapted to EN 50288-7'] | [45 empty] | ['Annealed copper wires according to BS EN 60228'] | ['Polyvinyl chloride PVC'] |  |  |  |  | ['Aluminium / PETP tape over tinned copper drain wire'] |  |  | ['Polyvinyl chloride PVC'] | ['EN 60332-1-2'] | ['-30°C to +70°C'] | ['7.5 x cable diameter'] | ['500V', '*Also available in 300V variant on request.'] | ['Black, continuously numbered in white'] | ['1 layer of PETP tape']
[16 empty] | 0.5 | 2 | 7/0.3 |  |  | 20 | 250 |  | 2000 | [40 empty] | 36 | 25 | 1 | 2000
[16 empty] | 0.5 | 5 | 16/0.2 |  |  | 20 | 250 |  | 2000 | [40 empty] | 39 | 25 | 1 | 2000
[16 empty] | 0.75 | 2 | 7/0.37 |  |  | 20 | 250 |  | 2000 | [40 empty] | 24.5 | 25 | 1 | 2000
[16 empty] | 0.75 | 5 | 24/0.2 |  |  | 20 | 250 |  | 2000 | [40 empty] | 26 | 25 | 1 | 2000
[16 empty] | 1 | 2 | 7/0.43 |  |  | 20 | 250 |  | 2000 | [40 empty] | 18.1 | 25 | 1 | 2000
[16 empty] | 1 | 5 | 32/0.2 |  |  | 20 | 250 |  | 2000 | [40 empty] | 19.5 | 25 | 1 | 2000
[16 empty] | 1.5 | 2 | 7/0.53 |  |  | 20 | 250 |  | 2000 | [40 empty] | 12.1 | 40 | 1 | 2000
[16 empty] | 2.5 | 2 | 7/0.67 |  |  | 20 | 250 |  | 2000 | [40 empty] | 7.41 | 60 | 1 | 2000
[26 empty] | Class 5 Conductor | 70950221050 |  |  |  | 6.2 | 47.1 | [8 empty] | 0.44 | [27 empty] | 2×0.5 | 1
[26 empty] | Class 5 Conductor | 70950421050 |  |  |  | 7.1 | 70.7 | [8 empty] | 0.44 | [27 empty] | 4×0.5 | 1
[26 empty] | Class 5 Conductor | 70950521050 |  |  |  | 7.7 | 83.6 | [8 empty] | 0.44 | [27 empty] | 5×0.5 | 1
[26 empty] | Class 5 Conductor | 70950821050 |  |  |  | 9.4 | 121.8 | [8 empty] | 0.44 | [27 empty] | 8×0.5 | 1.1
[26 empty] | Class 5 Conductor | 70951021050 |  |  |  | 10.7 | 148.8 | [8 empty] | 0.44 | [27 empty] | 10×0.5 | 1.1
[26 empty] | Class 5 Conductor | 70951221050 |  |  |  | 11.1 | 169.7 | [8 empty] | 0.44 | [27 empty] | 12×0.5 | 1.2
[26 empty] | Class 5 Conductor | 70951621050 |  |  |  | 12.3 | 215.5 | [8 empty] | 0.44 | [27 empty] | 16×0.5 | 1.2
[26 empty] | Class 5 Conductor | 70952021050 |  |  |  | 13.7 | 263.8 | [8 empty] | 0.44 | [27 empty] | 20×0.5 | 1.3
[26 empty] | Class 5 Conductor | 70952421050 |  |  |  | 15.2 | 322.4 | [8 empty] | 0.44 | [27 empty] | 24×0.5 | 1.3
[26 empty] | Class 5 Conductor | 70950221075 |  |  |  | 6.6 | 55.4 | [8 empty] | 0.44 | [27 empty] | 2×0.75 | 1
[26 empty] | Class 5 Conductor | 70950421075 |  |  |  | 7.6 | 85.7 | [8 empty] | 0.44 | [27 empty] | 4×0.75 | 1
[26 empty] | Class 5 Conductor | 70950521075 |  |  |  | 8.3 | 102 | [8 empty] | 0.44 | [27 empty] | 5×0.75 | 1.1
[26 empty] | Class 5 Conductor | 70950821075 |  |  |  | 10.2 | 150.5 | [8 empty] | 0.44 | [27 empty] | 8×0.75 | 1.1
[26 empty] | Class 5 Conductor | 70951021075 |  |  |  | 11.6 | 184.8 | [8 empty] | 0.44 | [27 empty] | 10×0.75 | 1.2
[26 empty] | Class 5 Conductor | 70951221075 |  |  |  | 11.9 | 212.1 | [8 empty] | 0.44 | [27 empty] | 12×0.75 | 1.2
[26 empty] | Class 5 Conductor | 70951621075 |  |  |  | 13.3 | 295.4 | [8 empty] | 0.44 | [27 empty] | 16×0.75 | 1.2
[26 empty] | Class 5 Conductor | 70952021075 |  |  |  | 14.9 | 333.2 | [8 empty] | 0.44 | [27 empty] | 20×0.75 | 1.3
[26 empty] | Class 5 Conductor | 70952421075 |  |  |  | 16.5 | 408.7 | [8 empty] | 0.44 | [27 empty] | 24×0.75 | 1.4
[26 empty] | Class 5 Conductor | 70950220001 |  |  |  | 6.9 | 62.7 | [8 empty] | 0.44 | [27 empty] | 2×1 | 1
[26 empty] | Class 5 Conductor | 70950420001 |  |  |  | 8 | 99.1 | [8 empty] | 0.44 | [27 empty] | 4×1 | 1
[26 empty] | Class 5 Conductor | 70950520001 |  |  |  | 8.8 | 118.6 | [8 empty] | 0.44 | [27 empty] | 5×1 | 1.1
[26 empty] | Class 5 Conductor | 70950820001 |  |  |  | 10.7 | 176.5 | [8 empty] | 0.44 | [27 empty] | 8×1 | 1.1
[26 empty] | Class 5 Conductor | 70951020001 |  |  |  | 12.2 | 217.4 | [8 empty] | 0.44 | [27 empty] | 10×1 | 1.2
[26 empty] | Class 5 Conductor | 70951220001 |  |  |  | 12.6 | 250.5 | [8 empty] | 0.44 | [27 empty] | 12×1 | 1.2
[26 empty] | Class 5 Conductor | 70951620001 |  |  |  | 14.1 | 351.5 | [8 empty] | 0.44 | [27 empty] | 16×1 | 1.3
[26 empty] | Class 5 Conductor | 70952020001 |  |  |  | 15.7 | 396.4 | [8 empty] | 0.44 | [27 empty] | 20×1 | 1.3
[26 empty] | Class 5 Conductor | 70952420001 |  |  |  | 17.5 | 487.4 | [8 empty] | 0.44 | [27 empty] | 24×1 | 1.4
[26 empty] | Class 2 Conductor | 70920221050 |  |  |  | 6.2 | 46.9 | [8 empty] | 0.44 | [27 empty] | 2×0.5 | 1
[26 empty] | Class 2 Conductor | 70920421050 |  |  |  | 7.1 | 70.4 | [8 empty] | 0.44 | [27 empty] | 4×0.5 | 1
[26 empty] | Class 2 Conductor | 70920521050 |  |  |  | 7.7 | 83.3 | [8 empty] | 0.44 | [27 empty] | 5×0.5 | 1
[26 empty] | Class 2 Conductor | 70920821050 |  |  |  | 9.4 | 121.2 | [8 empty] | 0.44 | [27 empty] | 8×0.5 | 1.1
[26 empty] | Class 2 Conductor | 70921021050 |  |  |  | 10.7 | 148.1 | [8 empty] | 0.44 | [27 empty] | 10×0.5 | 1.1
[26 empty] | Class 2 Conductor | 70921221050 |  |  |  | 11.1 | 168.9 | [8 empty] | 0.44 | [27 empty] | 12×0.5 | 1.2
[26 empty] | Class 2 Conductor | 70921621050 |  |  |  | 12.3 | 214.4 | [8 empty] | 0.44 | [27 empty] | 16×0.5 | 1.2
[26 empty] | Class 2 Conductor | 70922021050 |  |  |  | 13.7 | 262.5 | [8 empty] | 0.44 | [27 empty] | 20×0.5 | 1.3
[26 empty] | Class 2 Conductor | 70922421050 |  |  |  | 15.2 | 320.9 | [8 empty] | 0.44 | [27 empty] | 24×0.5 | 1.3
[26 empty] | Class 2 Conductor | 70920221075 |  |  |  | 6.6 | 55.5 | [8 empty] | 0.44 | [27 empty] | 2×0.75 | 1
[26 empty] | Class 2 Conductor | 70920421075 |  |  |  | 7.7 | 85.8 | [8 empty] | 0.44 | [27 empty] | 4×0.75 | 1
[26 empty] | Class 2 Conductor | 70920521075 |  |  |  | 8.4 | 102.2 | [8 empty] | 0.44 | [27 empty] | 5×0.75 | 1.1
[26 empty] | Class 2 Conductor | 70920821075 |  |  |  | 10.2 | 150.8 | [8 empty] | 0.44 | [27 empty] | 8×0.75 | 1.1
[26 empty] | Class 2 Conductor | 70921021075 |  |  |  | 11.6 | 185.2 | [8 empty] | 0.44 | [27 empty] | 10×0.75 | 1.2
[26 empty] | Class 2 Conductor | 70921221075 |  |  |  | 12 | 212.5 | [8 empty] | 0.44 | [27 empty] | 12×0.75 | 1.2
[26 empty] | Class 2 Conductor | 70921621075 |  |  |  | 13.3 | 296 | [8 empty] | 0.44 | [27 empty] | 16×0.75 | 1.2
[26 empty] | Class 2 Conductor | 70922021075 |  |  |  | 14.9 | 333.9 | [8 empty] | 0.44 | [27 empty] | 20×0.75 | 1.3
[26 empty] | Class 2 Conductor | 70922421075 |  |  |  | 16.6 | 409.6 | [8 empty] | 0.44 | [27 empty] | 24×0.75 | 1.4
[26 empty] | Class 2 Conductor | 70920220001 |  |  |  | 7 | 64.1 | [8 empty] | 0.44 | [27 empty] | 2×1 | 1
[26 empty] | Class 2 Conductor | 70920420001 |  |  |  | 8.2 | 101.4 | [8 empty] | 0.44 | [27 empty] | 4×1 | 1.1
[26 empty] | Class 2 Conductor | 70920520001 |  |  |  | 8.9 | 121.4 | [8 empty] | 0.44 | [27 empty] | 5×1 | 1.1
[26 empty] | Class 2 Conductor | 70920820001 |  |  |  | 10.9 | 180.9 | [8 empty] | 0.44 | [27 empty] | 8×1 | 1.2
[26 empty] | Class 2 Conductor | 70921020001 |  |  |  | 12.4 | 222.8 | [8 empty] | 0.44 | [27 empty] | 10×1 | 1.2
[26 empty] | Class 2 Conductor | 70921220001 |  |  |  | 12.8 | 256.8 | [8 empty] | 0.44 | [27 empty] | 12×1 | 1.2
[26 empty] | Class 2 Conductor | 70921620001 |  |  |  | 14.3 | 360.5 | [8 empty] | 0.44 | [27 empty] | 16×1 | 1.3
[26 empty] | Class 2 Conductor | 70922020001 |  |  |  | 16 | 406.6 | [8 empty] | 0.44 | [27 empty] | 20×1 | 1.3
[26 empty] | Class 2 Conductor | 70922420001 |  |  |  | 17.8 | 500 | [8 empty] | 0.44 | [27 empty] | 24×1 | 1.4
[26 empty] | Class 2 Conductor | 70920221105 |  |  |  | 7.7 | 80.5 | [8 empty] | 0.44 | [27 empty] | 2×1.5 | 1
[26 empty] | Class 2 Conductor | 70920421105 |  |  |  | 9 | 131.3 | [8 empty] | 0.44 | [27 empty] | 4×1.5 | 1.1
[26 empty] | Class 2 Conductor | 70920521105 |  |  |  | 9.9 | 158.3 | [8 empty] | 0.44 | [27 empty] | 5×1.5 | 1.1
[26 empty] | Class 2 Conductor | 70920821105 |  |  |  | 12.2 | 238.9 | [8 empty] | 0.44 | [27 empty] | 8×1.5 | 1.2
[26 empty] | Class 2 Conductor | 70921021105 |  |  |  | 13.8 | 295.5 | [8 empty] | 0.44 | [27 empty] | 10×1.5 | 1.3
[26 empty] | Class 2 Conductor | 70921221105 |  |  |  | 14.3 | 342.5 | [8 empty] | 0.44 | [27 empty] | 12×1.5 | 1.3
[26 empty] | Class 2 Conductor | 70921621105 |  |  |  | 16 | 442.6 | [8 empty] | 0.44 | [27 empty] | 16×1.5 | 1.3
[26 empty] | Class 2 Conductor | 70922021105 |  |  |  | 17.9 | 547.6 | [8 empty] | 0.44 | [27 empty] | 20×1.5 | 1.4
[26 empty] | Class 2 Conductor | 70922421105 |  |  |  | 20 | 675.5 | [8 empty] | 0.44 | [27 empty] | 24×1.5 | 1.5
[26 empty] | Class 2 Conductor | 70920221205 |  |  |  | 9.1 | 112.2 | [8 empty] | 0.53 | [27 empty] | 2×2.5 | 1.1
[26 empty] | Class 2 Conductor | 70920421205 |  |  |  | 10.6 | 189 | [8 empty] | 0.53 | [27 empty] | 4×2.5 | 1.1
[26 empty] | Class 2 Conductor | 70920521205 |  |  |  | 11.7 | 229.6 | [8 empty] | 0.53 | [27 empty] | 5×2.5 | 1.2
[26 empty] | Class 2 Conductor | 70920821205 |  |  |  | 14.5 | 350.9 | [8 empty] | 0.53 | [27 empty] | 8×2.5 | 1.3
[26 empty] | Class 2 Conductor | 70921021205 |  |  |  | 16.5 | 436 | [8 empty] | 0.53 | [27 empty] | 10×2.5 | 1.4
[26 empty] | Class 2 Conductor | 70921221205 |  |  |  | 17.1 | 508 | [8 empty] | 0.53 | [27 empty] | 12×2.5 | 1.4
[26 empty] | Class 2 Conductor | 70921621205 |  |  |  | 19.1 | 660.3 | [8 empty] | 0.53 | [27 empty] | 16×2.5 | 1.5
[26 empty] | Class 2 Conductor | 70922021205 |  |  |  | 21.5 | 819.7 | [8 empty] | 0.53 | [27 empty] | 20×2.5 | 1.5
[26 empty] | Class 2 Conductor | 70922421205 |  |  |  | 24 | 981 | [8 empty] | 0.53 | [27 empty] | 24×2.5 | 1.6
https://www.rrkabel.com/instrumentation-cable/instrumentation-cable-re-2xsty-multicore | RE-2X(St)Y – MULTICORE | ['https://www.rrkabel.com/Uploads/Products/88/ProductZoomForMoreDetailsImage/02.jpg', 'https://www.rrkabel.com/Uploads/Products/88/ProductZoomImage/03.jpg', 'https://www.rrkabel.com/Uploads/Products/262/ProductFeaturesDetails/01.png', 'https://www.rrkabel.com/Uploads/Products/262/ProductFeaturesDetails/01.png'] | ['Adapted to EN 50288-7'] | ['Annealed copper wires according to BS EN 60228'] | ['Cross-linked polyethylene XLPE'] |  |  | ['1 layer of PETP tape'] | ['Aluminium / PETP tape over tinned copper drain wire'] | ['Polyvinyl Chloride PVC (Also available in halogen free construction on request.)'] | ['EN 60332-1-2'] | ['-30°C to +90°C'] | ['7.5 x cable diameter'] | ['500V', '*Also available in 300V variant on request.'] | [56 empty] | ['Black, continuously numbered in white']
[16 empty] | 0.5 | 2 | 7/0.3 |  |  | 20 | 250 |  | 2000 | [40 empty] | 36 | 25 | 1 | 2000
[16 empty] | 0.5 | 5 | 16/0.2 |  |  | 20 | 250 |  | 2000 | [40 empty] | 39 | 25 | 1 | 2000
[16 empty] | 0.75 | 2 | 7/0.37 |  |  | 20 | 250 |  | 2000 | [40 empty] | 24.5 | 25 | 1 | 2000
[16 empty] | 0.75 | 5 | 24/0.2 |  |  | 20 | 250 |  | 2000 | [40 empty] | 26 | 25 | 1 | 2000
[16 empty] | 1 | 2 | 7/0.43 |  |  | 20 | 250 |  | 2000 | [40 empty] | 18.1 | 25 | 1 | 2000
[16 empty] | 1 | 5 | 32/0.2 |  |  | 20 | 250 |  | 2000 | [40 empty] | 19.5 | 25 | 1 | 2000
[16 empty] | 1.5 | 2 | 7/0.53 |  |  | 20 | 250 |  | 2000 | [40 empty] | 12.1 | 40 | 1 | 2000
[16 empty] | 2.5 | 2 | 7/0.67 |  |  | 20 | 250 |  | 2000 | [40 empty] | 7.41 | 60 | 1 | 2000
[26 empty] | Class 5 Conductor | 71050221050 |  |  |  | 6.2 | 43.9 | [8 empty] | 0.44 | [27 empty] | 2×0.5 | 1
[26 empty] | Class 5 Conductor | 71050421050 |  |  |  | 7.1 | 64.4 | [8 empty] | 0.44 | [27 empty] | 4×0.5 | 1
[26 empty] | Class 5 Conductor | 71050521050 |  |  |  | 7.7 | 75.7 | [8 empty] | 0.44 | [27 empty] | 5×0.5 | 1
[26 empty] | Class 5 Conductor | 71050821050 |  |  |  | 9.4 | 109.1 | [8 empty] | 0.44 | [27 empty] | 8×0.5 | 1.1
[26 empty] | Class 5 Conductor | 71051021050 |  |  |  | 10.7 | 132.9 | [8 empty] | 0.44 | [27 empty] | 10×0.5 | 1.1
[26 empty] | Class 5 Conductor | 71051221050 |  |  |  | 11.1 | 150.7 | [8 empty] | 0.44 | [27 empty] | 12×0.5 | 1.2
[26 empty] | Class 5 Conductor | 71051621050 |  |  |  | 12.3 | 190.1 | [8 empty] | 0.44 | [27 empty] | 16×0.5 | 1.2
[26 empty] | Class 5 Conductor | 71052021050 |  |  |  | 13.7 | 232.1 | [8 empty] | 0.44 | [27 empty] | 20×0.5 | 1.3
[26 empty] | Class 5 Conductor | 71052421050 |  |  |  | 15.2 | 282.8 | [8 empty] | 0.44 | [27 empty] | 24×0.5 | 1.3
[26 empty] | Class 5 Conductor | 71050221075 |  |  |  | 6.6 | 51.7 | [8 empty] | 0.44 | [27 empty] | 2×0.75 | 1
[26 empty] | Class 5 Conductor | 71050421075 |  |  |  | 7.6 | 78.4 | [8 empty] | 0.44 | [27 empty] | 4×0.75 | 1
[26 empty] | Class 5 Conductor | 71050521075 |  |  |  | 8.3 | 92.9 | [8 empty] | 0.44 | [27 empty] | 5×0.75 | 1.1
[26 empty] | Class 5 Conductor | 71050821075 |  |  |  | 10.2 | 136 | [8 empty] | 0.44 | [27 empty] | 8×0.75 | 1.1
[26 empty] | Class 5 Conductor | 71051021075 |  |  |  | 11.6 | 166.6 | [8 empty] | 0.44 | [27 empty] | 10×0.75 | 1.2
[26 empty] | Class 5 Conductor | 71051221075 |  |  |  | 11.9 | 190.2 | [8 empty] | 0.44 | [27 empty] | 12×0.75 | 1.2
[26 empty] | Class 5 Conductor | 71051621075 |  |  |  | 13.3 | 262.6 | [8 empty] | 0.44 | [27 empty] | 16×0.75 | 1.2
[26 empty] | Class 5 Conductor | 71052021075 |  |  |  | 14.9 | 296.8 | [8 empty] | 0.44 | [27 empty] | 20×0.75 | 1.3
[26 empty] | Class 5 Conductor | 71052421075 |  |  |  | 16.5 | 363.2 | [8 empty] | 0.44 | [27 empty] | 24×0.75 | 1.4
[26 empty] | Class 5 Conductor | 71050220001 |  |  |  | 6.9 | 58.8 | [8 empty] | 0.44 | [27 empty] | 2×1 | 1
[26 empty] | Class 5 Conductor | 71050420001 |  |  |  | 8 | 91.2 | [8 empty] | 0.44 | [27 empty] | 4×1 | 1
[26 empty] | Class 5 Conductor | 71050520001 |  |  |  | 8.8 | 108.7 | [8 empty] | 0.44 | [27 empty] | 5×1 | 1.1
[26 empty] | Class 5 Conductor | 71050820001 |  |  |  | 10.7 | 160.7 | [8 empty] | 0.44 | [27 empty] | 8×1 | 1.1
[26 empty] | Class 5 Conductor | 71051020001 |  |  |  | 12.2 | 197.5 | [8 empty] | 0.44 | [27 empty] | 10×1 | 1.2
[26 empty] | Class 5 Conductor | 71051220001 |  |  |  | 12.6 | 226.7 | [8 empty] | 0.44 | [27 empty] | 12×1 | 1.2
[26 empty] | Class 5 Conductor | 71051620001 |  |  |  | 14.1 | 315.8 | [8 empty] | 0.44 | [27 empty] | 16×1 | 1.3
[26 empty] | Class 5 Conductor | 71052020001 |  |  |  | 15.7 | 356.7 | [8 empty] | 0.44 | [27 empty] | 20×1 | 1.3
[26 empty] | Class 5 Conductor | 71052420001 |  |  |  | 17.5 | 437.7 | [8 empty] | 0.44 | [27 empty] | 24×1 | 1.4
[26 empty] | Class 2 Conductor | 71020221050 |  |  |  | 6.2 | 43.7 | [8 empty] | 0.44 | [27 empty] | 2×0.5 | 1
[26 empty] | Class 2 Conductor | 71020421050 |  |  |  | 7.1 | 64.1 | [8 empty] | 0.44 | [27 empty] | 4×0.5 | 1
[26 empty] | Class 2 Conductor | 71020521050 |  |  |  | 7.7 | 75.3 | [8 empty] | 0.44 | [27 empty] | 5×0.5 | 1
[26 empty] | Class 2 Conductor | 71020821050 |  |  |  | 9.4 | 108.5 | [8 empty] | 0.44 | [27 empty] | 8×0.5 | 1.1
[26 empty] | Class 2 Conductor | 71021021050 |  |  |  | 10.7 | 132.2 | [8 empty] | 0.44 | [27 empty] | 10×0.5 | 1.1
[26 empty] | Class 2 Conductor | 71021221050 |  |  |  | 11.1 | 149.9 | [8 empty] | 0.44 | [27 empty] | 12×0.5 | 1.2
[26 empty] | Class 2 Conductor | 71021621050 |  |  |  | 12.3 | 189 | [8 empty] | 0.44 | [27 empty] | 16×0.5 | 1.2
[26 empty] | Class 2 Conductor | 71022021050 |  |  |  | 13.7 | 230.7 | [8 empty] | 0.44 | [27 empty] | 20×0.5 | 1.3
[26 empty] | Class 2 Conductor | 71022421050 |  |  |  | 15.2 | 281.1 | [8 empty] | 0.44 | [27 empty] | 24×0.5 | 1.3
[26 empty] | Class 2 Conductor | 71020221075 |  |  |  | 6.6 | 51.8 | [8 empty] | 0.44 | [27 empty] | 2×0.75 | 1
[26 empty] | Class 2 Conductor | 71020421075 |  |  |  | 7.7 | 78.5 | [8 empty] | 0.44 | [27 empty] | 4×0.75 | 1
[26 empty] | Class 2 Conductor | 71020521075 |  |  |  | 8.4 | 93 | [8 empty] | 0.44 | [27 empty] | 5×0.75 | 1.1
[26 empty] | Class 2 Conductor | 71020821075 |  |  |  | 10.2 | 136.1 | [8 empty] | 0.44 | [27 empty] | 8×0.75 | 1.1
[26 empty] | Class 2 Conductor | 71021021075 |  |  |  | 11.6 | 166.7 | [8 empty] | 0.44 | [27 empty] | 10×0.75 | 1.2
[26 empty] | Class 2 Conductor | 71021221075 |  |  |  | 12 | 190.4 | [8 empty] | 0.44 | [27 empty] | 12×0.75 | 1.2
[26 empty] | Class 2 Conductor | 71021621075 |  |  |  | 13.3 | 262.8 | [8 empty] | 0.44 | [27 empty] | 16×0.75 | 1.2
[26 empty] | Class 2 Conductor | 71022021075 |  |  |  | 14.9 | 297 | [8 empty] | 0.44 | [27 empty] | 20×0.75 | 1.3
[26 empty] | Class 2 Conductor | 71022421075 |  |  |  | 16.6 | 363.5 | [8 empty] | 0.44 | [27 empty] | 24×0.75 | 1.4
[26 empty] | Class 2 Conductor | 71020220001 |  |  |  | 7 | 59.9 | [8 empty] | 0.44 | [27 empty] | 2×1 | 1
[26 empty] | Class 2 Conductor | 71020420001 |  |  |  | 8.2 | 93 | [8 empty] | 0.44 | [27 empty] | 4×1 | 1.1
[26 empty] | Class 2 Conductor | 71020520001 |  |  |  | 8.9 | 111 | [8 empty] | 0.44 | [27 empty] | 5×1 | 1.1
[26 empty] | Class 2 Conductor | 71020820001 |  |  |  | 10.9 | 164.2 | [8 empty] | 0.44 | [27 empty] | 8×1 | 1.2
[26 empty] | Class 2 Conductor | 71021020001 |  |  |  | 12.4 | 202 | [8 empty] | 0.44 | [27 empty] | 10×1 | 1.2
[26 empty] | Class 2 Conductor | 71021220001 |  |  |  | 12.8 | 231.8 | [8 empty] | 0.44 | [27 empty] | 12×1 | 1.2
[26 empty] | Class 2 Conductor | 71021620001 |  |  |  | 14.3 | 323 | [8 empty] | 0.44 | [27 empty] | 16×1 | 1.3
[26 empty] | Class 2 Conductor | 71022020001 |  |  |  | 16 | 364.9 | [8 empty] | 0.44 | [27 empty] | 20×1 | 1.3
[26 empty] | Class 2 Conductor | 71022420001 |  |  |  | 17.8 | 447.9 | [8 empty] | 0.44 | [27 empty] | 24×1 | 1.4
[26 empty] | Class 2 Conductor | 71020221105 |  |  |  | 7.7 | 75.4 | [8 empty] | 0.44 | [27 empty] | 2×1.5 | 1
[26 empty] | Class 2 Conductor | 71020421105 |  |  |  | 9 | 121.1 | [8 empty] | 0.44 | [27 empty] | 4×1.5 | 1.1
[26 empty] | Class 2 Conductor | 71020521105 |  |  |  | 9.9 | 145.6 | [8 empty] | 0.44 | [27 empty] | 5×1.5 | 1.1
[26 empty] | Class 2 Conductor | 71020821105 |  |  |  | 12.2 | 218.6 | [8 empty] | 0.44 | [27 empty] | 8×1.5 | 1.2
[26 empty] | Class 2 Conductor | 71021021105 |  |  |  | 13.8 | 270.1 | [8 empty] | 0.44 | [27 empty] | 10×1.5 | 1.3
[26 empty] | Class 2 Conductor | 71021221105 |  |  |  | 14.3 | 312 | [8 empty] | 0.44 | [27 empty] | 12×1.5 | 1.3
[26 empty] | Class 2 Conductor | 71021621105 |  |  |  | 16 | 401.9 | [8 empty] | 0.44 | [27 empty] | 16×1.5 | 1.3
[26 empty] | Class 2 Conductor | 71022021105 |  |  |  | 17.9 | 496.8 | [8 empty] | 0.44 | [27 empty] | 20×1.5 | 1.4
[26 empty] | Class 2 Conductor | 71022421105 |  |  |  | 20 | 612 | [8 empty] | 0.44 | [27 empty] | 24×1.5 | 1.5
[26 empty] | Class 2 Conductor | 71020221205 |  |  |  | 9.1 | 104.9 | [8 empty] | 0.53 | [27 empty] | 2×2.5 | 1.1
[26 empty] | Class 2 Conductor | 71020421205 |  |  |  | 10.6 | 174.3 | [8 empty] | 0.53 | [27 empty] | 4×2.5 | 1.1
[26 empty] | Class 2 Conductor | 71020521205 |  |  |  | 11.7 | 211.2 | [8 empty] | 0.53 | [27 empty] | 5×2.5 | 1.2
[26 empty] | Class 2 Conductor | 71020821205 |  |  |  | 14.5 | 321.5 | [8 empty] | 0.53 | [27 empty] | 8×2.5 | 1.3
[26 empty] | Class 2 Conductor | 71021021205 |  |  |  | 16.5 | 399.2 | [8 empty] | 0.53 | [27 empty] | 10×2.5 | 1.4
[26 empty] | Class 2 Conductor | 71021221205 |  |  |  | 17.1 | 463.8 | [8 empty] | 0.53 | [27 empty] | 12×2.5 | 1.4
[26 empty] | Class 2 Conductor | 71021621205 |  |  |  | 19.1 | 601.4 | [8 empty] | 0.53 | [27 empty] | 16×2.5 | 1.5
[26 empty] | Class 2 Conductor | 71022021205 |  |  |  | 21.5 | 746.1 | [8 empty] | 0.53 | [27 empty] | 20×2.5 | 1.5
[26 empty] | Class 2 Conductor | 71022421205 |  |  |  | 24 | 892.6 | [8 empty] | 0.53 | [27 empty] | 24×2.5 | 1.6
https://www.rrkabel.com/instrumentation-cable/instrumentation-cable-re-ystysway-multicore | RE-Y(St)YSWAY – MULTICORE | ['https://www.rrkabel.com/Uploads/Products/89/ProductZoomForMoreDetailsImage/02.jpg', 'https://www.rrkabel.com/Uploads/Products/89/ProductZoomImage/03.jpg', 'https://www.rrkabel.com/Uploads/Products/265/ProductFeaturesDetails/01.png', 'https://www.rrkabel.com/Uploads/Products/265/ProductFeaturesDetails/01.png'] | ['Adapted to EN 50288-7'] | [45 empty] | ['Annealed copper wires according to BS EN 60228'] | ['Polyvinyl chloride PVC'] |  |  |  |  | ['Aluminium / PETP tape over tinned copper drain wire'] | ['Polyvinyl chloride PVC'] | ['Galvanised round steel wires'] | ['Polyvinyl chloride PVC'] | ['EN 60332-1-2'] | ['-30°C to +70°C'] | ['10 x cable diameter'] | ['500V', '*Also available in 300V variant on request'] | ['Black, continuously numbered in white'] | ['1 layer of PETP tape']
[16 empty] | 0.5 | 2 | 7/0.3 |  |  | 20 | 250 |  | 2000 | [40 empty] | 36 | 25 | 1 | 2000
[16 empty] | 0.5 | 5 | 16/0.2 |  |  | 20 | 250 |  | 2000 | [40 empty] | 39 | 25 | 1 | 2000
[16 empty] | 0.75 | 2 | 7/0.37 |  |  | 20 | 250 |  | 2000 | [40 empty] | 24.5 | 25 | 1 | 2000
[16 empty] | 0.75 | 5 | 24/0.2 |  |  | 20 | 250 |  | 2000 | [40 empty] | 26 | 25 | 1 | 2000
[16 empty] | 1 | 2 | 7/0.43 |  |  | 20 | 250 |  | 2000 | [40 empty] | 18.1 | 25 | 1 | 2000
[16 empty] | 1 | 5 | 32/0.2 |  |  | 20 | 250 |  | 2000 | [40 empty] | 19.5 | 25 | 1 | 2000
[16 empty] | 1.5 | 2 | 7/0.53 |  |  | 20 | 250 |  | 2000 | [40 empty] | 12.1 | 40 | 1 | 2000
[16 empty] | 2.5 | 2 | 7/0.67 |  |  | 20 | 250 |  | 2000 | [40 empty] | 7.41 | 60 | 1 | 2000
[26 empty] | Class 5 Conductor | 71150221050 |  |  |  | 10.8 | 206.9 | [8 empty] | 0.44 | 1 |  |  | 1.4 |  |  | 0.9 | [20 empty] | 2×0.5 |  |  | 6.2
[26 empty] | Class 5 Conductor | 71150421050 |  |  |  | 11.8 | 250.4 | [8 empty] | 0.44 | 1 |  |  | 1.4 |  |  | 0.9 | [20 empty] | 4×0.5 |  |  | 7.1
[26 empty] | Class 5 Conductor | 71150521050 |  |  |  | 12.4 | 276.4 | [8 empty] | 0.44 | 1 |  |  | 1.5 |  |  | 0.9 | [20 empty] | 5×0.5 |  |  | 7.7
[26 empty] | Class 5 Conductor | 71150821050 |  |  |  | 14.1 | 349.6 | [8 empty] | 0.44 | 1 |  |  | 1.5 |  |  | 0.9 | [20 empty] | 8×0.5 |  |  | 9.2
[26 empty] | Class 5 Conductor | 71151021050 |  |  |  | 15.3 | 402.1 | [8 empty] | 0.44 | 1 |  |  | 1.5 |  |  | 0.9 | [20 empty] | 10×0.5 |  |  | 10.4
[26 empty] | Class 5 Conductor | 71151221050 |  |  |  | 15.6 | 430.4 | [8 empty] | 0.44 | 1 |  |  | 1.6 |  |  | 0.9 | [20 empty] | 12×0.5 |  |  | 10.7
[26 empty] | Class 5 Conductor | 71151621050 |  |  |  | 16.8 | 501 | [8 empty] | 0.44 | 1 |  |  | 1.6 |  |  | 0.9 | [20 empty] | 16×0.5 |  |  | 11.9
[26 empty] | Class 5 Conductor | 71152021050 |  |  |  | 18.2 | 578.1 | [8 empty] | 0.44 | 1 |  |  | 1.6 |  |  | 0.9 | [20 empty] | 20×0.5 |  |  | 13.2
[26 empty] | Class 5 Conductor | 71152421050 |  |  |  | 19.7 | 667.1 | [8 empty] | 0.44 | 1 |  |  | 1.7 |  |  | 0.9 | [20 empty] | 24×0.5 |  |  | 14.6
[26 empty] | Class 5 Conductor | 71150221075 |  |  |  | 11.3 | 224.2 | [8 empty] | 0.44 | 1 |  |  | 1.4 |  |  | 0.9 | [20 empty] | 2×0.75 |  |  | 6.6
[26 empty] | Class 5 Conductor | 71150421075 |  |  |  | 12.3 | 276.2 | [8 empty] | 0.44 | 1 |  |  | 1.5 |  |  | 0.9 | [20 empty] | 4×0.75 |  |  | 7.6
[26 empty] | Class 5 Conductor | 71150521075 |  |  |  | 13 | 306.9 | [8 empty] | 0.44 | 1 |  |  | 1.5 |  |  | 0.9 | [20 empty] | 5×0.75 |  |  | 8.2
[26 empty] | Class 5 Conductor | 71150821075 |  |  |  | 14.8 | 393.6 | [8 empty] | 0.44 | 1 |  |  | 1.5 |  |  | 0.9 | [20 empty] | 8×0.75 |  |  | 9.9
[26 empty] | Class 5 Conductor | 71151021075 |  |  |  | 16.1 | 455.7 | [8 empty] | 0.44 | 1 |  |  | 1.6 |  |  | 0.9 | [20 empty] | 10×0.75 |  |  | 11.2
[26 empty] | Class 5 Conductor | 71151221075 |  |  |  | 16.5 | 491 | [8 empty] | 0.44 | 1 |  |  | 1.6 |  |  | 0.9 | [20 empty] | 12×0.75 |  |  | 11.6
[26 empty] | Class 5 Conductor | 71151621075 |  |  |  | 17.8 | 601.4 | [8 empty] | 0.44 | 1 |  |  | 1.6 |  |  | 0.9 | [20 empty] | 16×0.75 |  |  | 12.8
[26 empty] | Class 5 Conductor | 71152021075 |  |  |  | 19.4 | 670.5 | [8 empty] | 0.44 | 1 |  |  | 1.6 |  |  | 0.9 | [20 empty] | 20×0.75 |  |  | 14.3
[26 empty] | Class 5 Conductor | 71152421075 |  |  |  | 21.7 | 880.8 | [8 empty] | 0.44 | 1 |  |  | 1.7 |  |  | 1.25 | [20 empty] | 24×0.75 |  |  | 15.8
[26 empty] | Class 5 Conductor | 71150220001 |  |  |  | 11.6 | 238.3 | [8 empty] | 0.44 | 1 |  |  | 1.4 |  |  | 0.9 | [20 empty] | 2×1 |  |  | 6.9
[26 empty] | Class 5 Conductor | 71150420001 |  |  |  | 12.7 | 297.7 | [8 empty] | 0.44 | 1 |  |  | 1.5 |  |  | 0.9 | [20 empty] | 4×1 |  |  | 7.9
[26 empty] | Class 5 Conductor | 71150520001 |  |  |  | 13.4 | 332.5 | [8 empty] | 0.44 | 1 |  |  | 1.5 |  |  | 0.9 | [20 empty] | 5×1 |  |  | 8.6
[26 empty] | Class 5 Conductor | 71150820001 |  |  |  | 15.3 | 431 | [8 empty] | 0.44 | 1 |  |  | 1.5 |  |  | 0.9 | [20 empty] | 8×1 |  |  | 10.5
[26 empty] | Class 5 Conductor | 71151020001 |  |  |  | 16.8 | 501.4 | [8 empty] | 0.44 | 1 |  |  | 1.6 |  |  | 0.9 | [20 empty] | 10×1 |  |  | 11.8
[26 empty] | Class 5 Conductor | 71151220001 |  |  |  | 17.2 | 543 | [8 empty] | 0.44 | 1 |  |  | 1.6 |  |  | 0.9 | [20 empty] | 12×1 |  |  | 12.2
[26 empty] | Class 5 Conductor | 71151620001 |  |  |  | 18.6 | 672.8 | [8 empty] | 0.44 | 1 |  |  | 1.6 |  |  | 0.9 | [20 empty] | 16×1 |  |  | 13.5
[26 empty] | Class 5 Conductor | 71152020001 |  |  |  | 20.9 | 848.1 | [8 empty] | 0.44 | 1 |  |  | 1.7 |  |  | 1.25 | [20 empty] | 20×1 |  |  | 15.1
[26 empty] | Class 5 Conductor | 71152420001 |  |  |  | 22.7 | 984.2 | [8 empty] | 0.44 | 1 |  |  | 1.7 |  |  | 1.25 | [20 empty] | 24×1 |  |  | 16.7
[26 empty] | Class 2 Conductor | 71120221050 |  |  |  | 10.8 | 206.7 | [8 empty] | 0.44 | 1 |  |  | 1.4 |  |  | 0.9 | [20 empty] | 2×0.5 |  |  | 6.2
[26 empty] | Class 2 Conductor | 71120421050 |  |  |  | 11.8 | 250.1 | [8 empty] | 0.44 | 1 |  |  | 1.4 |  |  | 0.9 | [20 empty] | 4×0.5 |  |  | 7.1
[26 empty] | Class 2 Conductor | 71120521050 |  |  |  | 12.4 | 276.1 | [8 empty] | 0.44 | 1 |  |  | 1.5 |  |  | 0.9 | [20 empty] | 5×0.5 |  |  | 7.7
[26 empty] | Class 2 Conductor | 71120821050 |  |  |  | 14.1 | 349.1 | [8 empty] | 0.44 | 1 |  |  | 1.5 |  |  | 0.9 | [20 empty] | 8×0.5 |  |  | 9.2
[26 empty] | Class 2 Conductor | 71121021050 |  |  |  | 15.3 | 401.4 | [8 empty] | 0.44 | 1 |  |  | 1.5 |  |  | 0.9 | [20 empty] | 1×0.5 |  |  | 10.4
[26 empty] | Class 2 Conductor | 71121221050 |  |  |  | 15.6 | 429.6 | [8 empty] | 0.44 | 1 |  |  | 1.6 |  |  | 0.9 | [20 empty] | 12×0.5 |  |  | 10.7
[26 empty] | Class 2 Conductor | 71121621050 |  |  |  | 16.8 | 500 | [8 empty] | 0.44 | 1 |  |  | 1.6 |  |  | 0.9 | [20 empty] | 16×0.5 |  |  | 11.9
[26 empty] | Class 2 Conductor | 71122021050 |  |  |  | 18.2 | 576.8 | [8 empty] | 0.44 | 1 |  |  | 1.6 |  |  | 0.9 | [20 empty] | 20×0.5 |  |  | 13.2
[26 empty] | Class 2 Conductor | 71122421050 |  |  |  | 19.7 | 665.5 | [8 empty] | 0.44 | 1 |  |  | 1.7 |  |  | 0.9 | [20 empty] | 24×0.5 |  |  | 14.6
[26 empty] | Class 2 Conductor | 71120221075 |  |  |  | 11.3 | 224.7 | [8 empty] | 0.44 | 1 |  |  | 1.4 |  |  | 0.9 | [20 empty] | 2×0.75 |  |  | 6.6
[26 empty] | Class 2 Conductor | 71120421075 |  |  |  | 12.3 | 276.8 | [8 empty] | 0.44 | 1 |  |  | 1.5 |  |  | 0.9 | [20 empty] | 4×0.75 |  |  | 7.6
[26 empty] | Class 2 Conductor | 71120521075 |  |  |  | 13 | 307.7 | [8 empty] | 0.44 | 1 |  |  | 1.5 |  |  | 0.9 | [20 empty] | 5×0.75 |  |  | 8.2
[26 empty] | Class 2 Conductor | 71120821075 |  |  |  | 14.8 | 394.7 | [8 empty] | 0.44 | 1 |  |  | 1.5 |  |  | 0.9 | [20 empty] | 8×0.75 |  |  | 10
[26 empty] | Class 2 Conductor | 71121021075 |  |  |  | 16.2 | 456.9 | [8 empty] | 0.44 | 1 |  |  | 1.6 |  |  | 0.9 | [20 empty] | 10×0.75 |  |  | 11.2
[26 empty] | Class 2 Conductor | 71121221075 |  |  |  | 16.6 | 492.3 | [8 empty] | 0.44 | 1 |  |  | 1.6 |  |  | 0.9 | [20 empty] | 12×0.75 |  |  | 11.6
[26 empty] | Class 2 Conductor | 71121621075 |  |  |  | 17.9 | 603 | [8 empty] | 0.44 | 1 |  |  | 1.6 |  |  | 0.9 | [20 empty] | 16×0.75 |  |  | 12.9
[26 empty] | Class 2 Conductor | 71122021075 |  |  |  | 19.4 | 672.3 | [8 empty] | 0.44 | 1 |  |  | 1.7 |  |  | 0.9 | [20 empty] | 20×0.75 |  |  | 14.3
[26 empty] | Class 2 Conductor | 71122421075 |  |  |  | 21.8 | 883.4 | [8 empty] | 0.44 | 1 |  |  | 1.7 |  |  | 1.25 | [20 empty] | 24×0.75 |  |  | 15.9
[26 empty] | Class 2 Conductor | 71120220001 |  |  |  | 11.7 | 241.9 | [8 empty] | 0.44 | 1 |  |  | 1.4 |  |  | 0.9 | [20 empty] | 2×1 |  |  | 7
[26 empty] | Class 2 Conductor | 71120420001 |  |  |  | 12.8 | 302.7 | [8 empty] | 0.44 | 1 |  |  | 1.5 |  |  | 0.9 | [20 empty] | 4×1 |  |  | 8.1
[26 empty] | Class 2 Conductor | 71120520001 |  |  |  | 13.5 | 338.2 | [8 empty] | 0.44 | 1 |  |  | 1.5 |  |  | 0.9 | [20 empty] | 5×1 |  |  | 8.8
[26 empty] | Class 2 Conductor | 71120820001 |  |  |  | 15.5 | 439.1 | [8 empty] | 0.44 | 1 |  |  | 1.5 |  |  | 0.9 | [20 empty] | 8×1 |  |  | 10.6
[26 empty] | Class 2 Conductor | 71121020001 |  |  |  | 17 | 511.1 | [8 empty] | 0.44 | 1 |  |  | 1.6 |  |  | 0.9 | [20 empty] | 10×1 |  |  | 12
[26 empty] | Class 2 Conductor | 71121220001 |  |  |  | 17.4 | 553.9 | [8 empty] | 0.44 | 1 |  |  | 1.6 |  |  | 0.9 | [20 empty] | 12×1 |  |  | 12.4
[26 empty] | Class 2 Conductor | 71121620001 |  |  |  | 18.8 | 686.8 | [8 empty] | 0.44 | 1 |  |  | 1.6 |  |  | 0.9 | [20 empty] | 16×1 |  |  | 13.8
[26 empty] | Class 2 Conductor | 71122020001 |  |  |  | 21.2 | 865.7 | [8 empty] | 0.44 | 1 |  |  | 1.7 |  |  | 1.25 | [20 empty] | 20×1 |  |  | 15.3
[26 empty] | Class 2 Conductor | 71122420001 |  |  |  | 23.4 | 1034.6 | [8 empty] | 0.44 | 1.2 |  |  | 1.8 |  |  | 1.25 | [20 empty] | 24×1 |  |  | 17.4
[26 empty] | Class 2 Conductor | 71120221105 |  |  |  | 12.4 | 273.1 | [8 empty] | 0.44 | 1 |  |  | 1.5 |  |  | 0.9 | [20 empty] | 2×1.5 |  |  | 7.7
[26 empty] | Class 2 Conductor | 71120421105 |  |  |  | 13.6 | 350.3 | [8 empty] | 0.44 | 1 |  |  | 1.5 |  |  | 0.9 | [20 empty] | 4×1.5 |  |  | 8.8
[26 empty] | Class 2 Conductor | 71120521105 |  |  |  | 14.5 | 394.9 | [8 empty] | 0.44 | 1 |  |  | 1.5 |  |  | 0.9 | [20 empty] | 5×1.5 |  |  | 9.6
[26 empty] | Class 2 Conductor | 71120821105 |  |  |  | 16.7 | 522.1 | [8 empty] | 0.44 | 1 |  |  | 1.6 |  |  | 0.9 | [20 empty] | 8×1.5 |  |  | 11.8
[26 empty] | Class 2 Conductor | 71121021105 |  |  |  | 18.4 | 612.5 | [8 empty] | 0.44 | 1 |  |  | 1.6 |  |  | 0.9 | [20 empty] | 10×1.5 |  |  | 13.3
[26 empty] | Class 2 Conductor | 71121221105 |  |  |  | 18.8 | 669.3 | [8 empty] | 0.44 | 1 |  |  | 1.6 |  |  | 0.9 | [20 empty] | 12×1.5 |  |  | 13.8
[26 empty] | Class 2 Conductor | 71121621105 |  |  |  | 21.2 | 901 | [8 empty] | 0.44 | 1 |  |  | 1.7 |  |  | 1.25 | [20 empty] | 16×1.5 |  |  | 15.3
[26 empty] | Class 2 Conductor | 71122021105 |  |  |  | 23.5 | 1084.5 | [8 empty] | 0.44 | 1.2 |  |  | 1.8 |  |  | 1.25 | [20 empty] | 20×1.5 |  |  | 17.5
[26 empty] | Class 2 Conductor | 71122421105 |  |  |  | 25.5 | 1266.1 | [8 empty] | 0.44 | 1.2 |  |  | 1.8 |  |  | 1.25 | [20 empty] | 24×1.5 |  |  | 19.4
[26 empty] | Class 2 Conductor | 71120221205 |  |  |  | 13.7 | 332.4 | [8 empty] | 0.53 | 1 |  |  | 1.5 |  |  | 0.9 | [20 empty] | 2×2.5 |  |  | 8.9
[26 empty] | Class 2 Conductor | 71120421205 |  |  |  | 15.2 | 441.2 | [8 empty] | 0.53 | 1 |  |  | 1.5 |  |  | 0.9 | [20 empty] | 4×2.5 |  |  | 10.3
[26 empty] | Class 2 Conductor | 71120521205 |  |  |  | 16.2 | 503 | [8 empty] | 0.53 | 1 |  |  | 1.6 |  |  | 0.9 | [20 empty] | 5×2.5 |  |  | 11.3
[26 empty] | Class 2 Conductor | 71120821205 |  |  |  | 19 | 680.5 | [8 empty] | 0.53 | 1 |  |  | 1.6 |  |  | 0.9 | [20 empty] | 8×2.5 |  |  | 13.9
[26 empty] | Class 2 Conductor | 71121021205 |  |  |  | 21.7 | 908.2 | [8 empty] | 0.53 | 1 |  |  | 1.7 |  |  | 1.25 | [20 empty] | 10×2.5 |  |  | 15.8
[26 empty] | Class 2 Conductor | 71121221205 |  |  |  | 22.3 | 995.3 | [8 empty] | 0.53 | 1 |  |  | 1.7 |  |  | 1.25 | [20 empty] | 12×2.5 |  |  | 16.4
[26 empty] | Class 2 Conductor | 71121621205 |  |  |  | 24.7 | 1229.3 | [8 empty] | 0.53 | 1.2 |  |  | 1.8 |  |  | 1.25 | [20 empty] | 16×2.5 |  |  | 18.6
[26 empty] | Class 2 Conductor | 71122021205 |  |  |  | 27 | 1449.9 | [8 empty] | 0.53 | 1.2 |  |  | 1.9 |  |  | 1.25 | [20 empty] | 20×2.5 |  |  | 20.8
[26 empty] | Class 2 Conductor | 71122421205 |  |  |  | 29.4 | 1675.5 | [8 empty] | 0.53 | 1.2 |  |  | 1.9 |  |  | 1.25 | [20 empty] | 24×2.5 |  |  | 23.1
https://www.rrkabel.com/instrumentation-cable/instrumentation-cable-re-2xstysway-multicore | RE-2X(St)YSWAY – MULTICORE | ['https://www.rrkabel.com/Uploads/Products/90/ProductZoomForMoreDetailsImage/02.jpg', 'https://www.rrkabel.com/Uploads/Products/90/ProductZoomImage/03.jpg', 'https://www.rrkabel.com/Uploads/Products/268/ProductFeaturesDetails/01.png', 'https://www.rrkabel.com/Uploads/Products/268/ProductFeaturesDetails/01.png'] | ['Adapted to EN 50288-7'] | [45 empty] | ['Annealed copper wires according to BS EN 60228'] | ['Cross-linked polyethylene XLPE'] |  |  |  |  | ['Aluminium / PETP tape over tinned copper drain wire'] | ['Polyvinyl chloride PVC'] | ['Galvanised round steel wires'] | ['Polyvinyl chloride PVC (Also available in halogen free construction, on request.)'] | ['EN 60332-1-2'] | ['-30°C to +90°C'] | ['10 x cable diameter'] | ['500V', '*Also available in 300V variant on request'] | ['Black, continuously numbered in white'] | ['1 layer of PETP tape']
[16 empty] | 0.5 | 2 | 7/0.3 |  | 25 | 5000 | 150 |  | 2000 | 2000 | [39 empty] | 36 |  | 1
[16 empty] | 0.5 | 5 | 16/0.2 |  | 25 | 5000 | 150 |  | 2000 | 2000 | [39 empty] | 39 |  | 1
[16 empty] | 0.75 | 2 | 7/0.37 |  | 25 | 5000 | 150 |  | 2000 | 2000 | [39 empty] | 24.5 |  | 1
[16 empty] | 0.75 | 5 | 24/0.2 |  | 25 | 5000 | 150 |  | 2000 | 2000 | [39 empty] | 26 |  | 1
[16 empty] | 1 | 2 | 7/0.43 |  | 25 | 5000 | 150 |  | 2000 | 2000 | [39 empty] | 18.1 |  | 1
[16 empty] | 1 | 5 | 32/0.2 |  | 25 | 5000 | 150 |  | 2000 | 2000 | [39 empty] | 19.5 |  | 1
[16 empty] | 1.5 | 2 | 7/0.53 |  | 40 | 5000 | 150 |  | 2000 | 2000 | [39 empty] | 12.1 |  | 1
[16 empty] | 2.5 | 2 | 7/0.67 |  | 60 | 5000 | 150 |  | 2000 | 2000 | [39 empty] | 7.41 |  | 1
[26 empty] | Class 5 Conductor | 71250221050 |  |  |  | 10.8 | 203.7 | [8 empty] | 0.44 | 1 | 6.2 | 0.9 | 1.4 | [23 empty] | 2×0.5
[26 empty] | Class 5 Conductor | 71250421050 |  |  |  | 11.8 | 244 | [8 empty] | 0.44 | 1 | 7.1 | 0.9 | 1.4 | [23 empty] | 4×0.5
[26 empty] | Class 5 Conductor | 71250521050 |  |  |  | 12.4 | 268.5 | [8 empty] | 0.44 | 1 | 7.7 | 0.9 | 1.5 | [23 empty] | 5×0.5
[26 empty] | Class 5 Conductor | 71250821050 |  |  |  | 14.1 | 336.9 | [8 empty] | 0.44 | 1 | 9.2 | 0.9 | 1.5 | [23 empty] | 8×0.5
[26 empty] | Class 5 Conductor | 71251021050 |  |  |  | 15.3 | 386.3 | [8 empty] | 0.44 | 1 | 10.4 | 0.9 | 1.5 | [23 empty] | 10×0.5
[26 empty] | Class 5 Conductor | 71251221050 |  |  |  | 15.6 | 411.4 | [8 empty] | 0.44 | 1 | 10.7 | 0.9 | 1.6 | [23 empty] | 12×0.5
[26 empty] | Class 5 Conductor | 71251621050 |  |  |  | 16.8 | 475.6 | [8 empty] | 0.44 | 1 | 11.9 | 0.9 | 1.6 | [23 empty] | 16×0.5
[26 empty] | Class 5 Conductor | 71252021050 |  |  |  | 18.2 | 546.4 | [8 empty] | 0.44 | 1 | 13.2 | 0.9 | 1.6 | [23 empty] | 20×0.5
[26 empty] | Class 5 Conductor | 71252421050 |  |  |  | 19.7 | 627.5 | [8 empty] | 0.44 | 1 | 14.6 | 0.9 | 1.7 | [23 empty] | 24×0.5
[26 empty] | Class 5 Conductor | 71250221075 |  |  |  | 11.3 | 220.6 | [8 empty] | 0.44 | 1 | 6.6 | 0.9 | 1.4 | [23 empty] | 2×0.75
[26 empty] | Class 5 Conductor | 71250421075 |  |  |  | 12.3 | 268.9 | [8 empty] | 0.44 | 1 | 7.6 | 0.9 | 1.5 | [23 empty] | 4×0.75
[26 empty] | Class 5 Conductor | 71250521075 |  |  |  | 13 | 297.8 | [8 empty] | 0.44 | 1 | 8.2 | 0.9 | 1.5 | [23 empty] | 5×0.75
[26 empty] | Class 5 Conductor | 71250821075 |  |  |  | 14.8 | 379.1 | [8 empty] | 0.44 | 1 | 9.9 | 0.9 | 1.5 | [23 empty] | 8×0.75
[26 empty] | Class 5 Conductor | 71251021075 |  |  |  | 16.1 | 437.5 | [8 empty] | 0.44 | 1 | 11.2 | 0.9 | 1.6 | [23 empty] | 10×0.75
[26 empty] | Class 5 Conductor | 71251221075 |  |  |  | 16.5 | 469.2 | [8 empty] | 0.44 | 1 | 11.6 | 0.9 | 1.6 | [23 empty] | 12×0.75
[26 empty] | Class 5 Conductor | 71251621075 |  |  |  | 17.8 | 568.6 | [8 empty] | 0.44 | 1 | 12.8 | 0.9 | 1.6 | [23 empty] | 16×0.75
[26 empty] | Class 5 Conductor | 71252021075 |  |  |  | 19.4 | 634.1 | [8 empty] | 0.44 | 1 | 14.3 | 0.9 | 1.6 | [23 empty] | 20×0.75
[26 empty] | Class 5 Conductor | 71252421075 |  |  |  | 21.7 | 835.3 | [8 empty] | 0.44 | 1 | 15.8 | 1.25 | 1.7 | [23 empty] | 24×0.75
[26 empty] | Class 5 Conductor | 71250220001 |  |  |  | 11.6 | 234.3 | [8 empty] | 0.44 | 1 | 6.9 | 0.9 | 1.4 | [23 empty] | 2×1
[26 empty] | Class 5 Conductor | 71250420001 |  |  |  | 12.7 | 289.7 | [8 empty] | 0.44 | 1 | 7.9 | 0.9 | 1.5 | [23 empty] | 4×1
[26 empty] | Class 5 Conductor | 71250520001 |  |  |  | 13.4 | 322.5 | [8 empty] | 0.44 | 1 | 8.6 | 0.9 | 1.5 | [23 empty] | 5×1
[26 empty] | Class 5 Conductor | 71250820001 |  |  |  | 15.3 | 415.1 | [8 empty] | 0.44 | 1 | 10.5 | 0.9 | 1.5 | [23 empty] | 8×1
[26 empty] | Class 5 Conductor | 71251020001 |  |  |  | 16.8 | 481.5 | [8 empty] | 0.44 | 1 | 11.8 | 0.9 | 1.6 | [23 empty] | 10×1
[26 empty] | Class 5 Conductor | 71251220001 |  |  |  | 17.2 | 519.2 | [8 empty] | 0.44 | 1 | 12.2 | 0.9 | 1.6 | [23 empty] | 12×1
[26 empty] | Class 5 Conductor | 71251620001 |  |  |  | 18.6 | 637.1 | [8 empty] | 0.44 | 1 | 13.5 | 0.9 | 1.6 | [23 empty] | 16×1
[26 empty] | Class 5 Conductor | 71252020001 |  |  |  | 20.9 | 808.4 | [8 empty] | 0.44 | 1 | 15.1 | 1.25 | 1.7 | [23 empty] | 20×1
[26 empty] | Class 5 Conductor | 71252420001 |  |  |  | 22.7 | 934.6 | [8 empty] | 0.44 | 1 | 16.7 | 1.25 | 1.7 | [23 empty] | 24×1
[26 empty] | Class 2 Conductor | 71220221050 |  |  |  | 10.8 | 203.5 | [8 empty] | 0.44 | 1 | 6.2 | 0.9 | 1.4 | [23 empty] | 2×0.5
[26 empty] | Class 2 Conductor | 71220421050 |  |  |  | 11.8 | 243.7 | [8 empty] | 0.44 | 1 | 7.1 | 0.9 | 1.4 | [23 empty] | 4×0.5
[26 empty] | Class 2 Conductor | 71220521050 |  |  |  | 12.4 | 268.1 | [8 empty] | 0.44 | 1 | 7.7 | 0.9 | 1.5 | [23 empty] | 5×0.5
[26 empty] | Class 2 Conductor | 71220821050 |  |  |  | 14.1 | 336.3 | [8 empty] | 0.44 | 1 | 9.2 | 0.9 | 1.5 | [23 empty] | 8×0.5
[26 empty] | Class 2 Conductor | 71221021050 |  |  |  | 15.3 | 385.5 | [8 empty] | 0.44 | 1 | 10.4 | 0.9 | 1.5 | [23 empty] | 10×0.5
[26 empty] | Class 2 Conductor | 71221221050 |  |  |  | 15.6 | 410.6 | [8 empty] | 0.44 | 1 | 10.7 | 0.9 | 1.6 | [23 empty] | 12×0.5
[26 empty] | Class 2 Conductor | 71221621050 |  |  |  | 16.8 | 474.5 | [8 empty] | 0.44 | 1 | 11.9 | 0.9 | 1.6 | [23 empty] | 16×0.5
[26 empty] | Class 2 Conductor | 71222021050 |  |  |  | 18.2 | 545 | [8 empty] | 0.44 | 1 | 13.2 | 0.9 | 1.6 | [23 empty] | 20×0.5
[26 empty] | Class 2 Conductor | 71222421050 |  |  |  | 19.7 | 625.8 | [8 empty] | 0.44 | 1 | 14.6 | 0.9 | 1.7 | [23 empty] | 24×0.5
[26 empty] | Class 2 Conductor | 71220221075 |  |  |  | 11.3 | 221.1 | [8 empty] | 0.44 | 1 | 6.6 | 0.9 | 1.4 | [23 empty] | 2×0.75
[26 empty] | Class 2 Conductor | 71220421075 |  |  |  | 12.3 | 269.5 | [8 empty] | 0.44 | 1 | 7.6 | 0.9 | 1.5 | [23 empty] | 4×0.75
[26 empty] | Class 2 Conductor | 71220521075 |  |  |  | 13 | 298.4 | [8 empty] | 0.44 | 1 | 8.2 | 0.9 | 1.5 | [23 empty] | 5×0.75
[26 empty] | Class 2 Conductor | 71220821075 |  |  |  | 14.8 | 379.9 | [8 empty] | 0.44 | 1 | 10 | 0.9 | 1.5 | [23 empty] | 8×0.75
[26 empty] | Class 2 Conductor | 71221021075 |  |  |  | 16.2 | 438.5 | [8 empty] | 0.44 | 1 | 11.2 | 0.9 | 1.6 | [23 empty] | 10×0.75
[26 empty] | Class 2 Conductor | 71221221075 |  |  |  | 16.6 | 470.2 | [8 empty] | 0.44 | 1 | 11.6 | 0.9 | 1.6 | [23 empty] | 12×0.75
[26 empty] | Class 2 Conductor | 71221621075 |  |  |  | 17.9 | 569.8 | [8 empty] | 0.44 | 1 | 12.9 | 0.9 | 1.6 | [23 empty] | 16×0.75
[26 empty] | Class 2 Conductor | 71222021075 |  |  |  | 19.4 | 635.5 | [8 empty] | 0.44 | 1 | 14.3 | 0.9 | 1.7 | [23 empty] | 20×0.75
[26 empty] | Class 2 Conductor | 71222421075 |  |  |  | 21.8 | 837.3 | [8 empty] | 0.44 | 1 | 15.9 | 1.25 | 1.7 | [23 empty] | 24×0.75
[26 empty] | Class 2 Conductor | 71220220001 |  |  |  | 11.7 | 237.7 | [8 empty] | 0.44 | 1 | 7 | 0.9 | 1.4 | [23 empty] | 2×1
[26 empty] | Class 2 Conductor | 71220420001 |  |  |  | 12.8 | 294.3 | [8 empty] | 0.44 | 1 | 8.1 | 0.9 | 1.5 | [23 empty] | 4×1
[26 empty] | Class 2 Conductor | 71220520001 |  |  |  | 13.5 | 327.8 | [8 empty] | 0.44 | 1 | 8.8 | 0.9 | 1.5 | [23 empty] | 5×1
[26 empty] | Class 2 Conductor | 71220820001 |  |  |  | 15.5 | 422.5 | [8 empty] | 0.44 | 1 | 10.6 | 0.9 | 1.5 | [23 empty] | 8×1
[26 empty] | Class 2 Conductor | 71221020001 |  |  |  | 17 | 490.3 | [8 empty] | 0.44 | 1 | 12 | 0.9 | 1.6 | [23 empty] | 10×1
[26 empty] | Class 2 Conductor | 71221220001 |  |  |  | 17.4 | 528.9 | [8 empty] | 0.44 | 1 | 12.4 | 0.9 | 1.6 | [23 empty] | 12×1
[26 empty] | Class 2 Conductor | 71221620001 |  |  |  | 18.8 | 649.3 | [8 empty] | 0.44 | 1 | 13.8 | 0.9 | 1.6 | [23 empty] | 16×1
[26 empty] | Class 2 Conductor | 71222020001 |  |  |  | 21.2 | 824 | [8 empty] | 0.44 | 1 | 15.3 | 1.25 | 1.7 | [23 empty] | 20×1
[26 empty] | Class 2 Conductor | 71222420001 |  |  |  | 23.4 | 982.5 | [8 empty] | 0.44 | 1.2 | 17.4 | 1.25 | 1.8 | [23 empty] | 24×1
[26 empty] | Class 2 Conductor | 71220221105 |  |  |  | 12.4 | 268 | [8 empty] | 0.44 | 1 | 7.7 | 0.9 | 1.5 | [23 empty] | 2×1.5
[26 empty] | Class 2 Conductor | 71220421105 |  |  |  | 13.6 | 340.2 | [8 empty] | 0.44 | 1 | 8.8 | 0.9 | 1.5 | [23 empty] | 4×1.5
[26 empty] | Class 2 Conductor | 71220521105 |  |  |  | 14.5 | 382.2 | [8 empty] | 0.44 | 1 | 9.6 | 0.9 | 1.5 | [23 empty] | 5×1.5
[26 empty] | Class 2 Conductor | 71220821105 |  |  |  | 16.7 | 501.8 | [8 empty] | 0.44 | 1 | 11.8 | 0.9 | 1.6 | [23 empty] | 8×1.5
[26 empty] | Class 2 Conductor | 71221021105 |  |  |  | 18.4 | 587.1 | [8 empty] | 0.44 | 1 | 13.3 | 0.9 | 1.6 | [23 empty] | 10×1.5
[26 empty] | Class 2 Conductor | 71221221105 |  |  |  | 18.8 | 638.9 | [8 empty] | 0.44 | 1 | 13.8 | 0.9 | 1.6 | [23 empty] | 12×1.5
[26 empty] | Class 2 Conductor | 71221621105 |  |  |  | 21.2 | 860.4 | [8 empty] | 0.44 | 1 | 15.3 | 1.25 | 1.7 | [23 empty] | 16×1.5
[26 empty] | Class 2 Conductor | 71222021105 |  |  |  | 23.5 | 1033.7 | [8 empty] | 0.44 | 1.2 | 17.5 | 1.25 | 1.8 | [23 empty] | 20×1.5
[26 empty] | Class 2 Conductor | 71222421105 |  |  |  | 25.5 | 1202.6 | [8 empty] | 0.44 | 1.2 | 19.4 | 1.25 | 1.8 | [23 empty] | 24×1.5
[26 empty] | Class 2 Conductor | 71220221205 |  |  |  | 13.7 | 325 | [8 empty] | 0.53 | 1 | 8.9 | 0.9 | 1.5 | [23 empty] | 2×2.5
[26 empty] | Class 2 Conductor | 71220421205 |  |  |  | 15.2 | 426.5 | [8 empty] | 0.53 | 1 | 10.3 | 0.9 | 1.5 | [23 empty] | 4×2.5
[26 empty] | Class 2 Conductor | 71220521205 |  |  |  | 16.2 | 484.6 | [8 empty] | 0.53 | 1 | 11.3 | 0.9 | 1.6 | [23 empty] | 5×2.5
[26 empty] | Class 2 Conductor | 71220821205 |  |  |  | 19 | 651.1 | [8 empty] | 0.53 | 1 | 13.9 | 0.9 | 1.6 | [23 empty] | 8×2.5
[26 empty] | Class 2 Conductor | 71221021205 |  |  |  | 21.7 | 871.3 | [8 empty] | 0.53 | 1 | 15.8 | 1.25 | 1.7 | [23 empty] | 10×2.5
[26 empty] | Class 2 Conductor | 71221221205 |  |  |  | 22.3 | 951.1 | [8 empty] | 0.53 | 1 | 16.4 | 1.25 | 1.7 | [23 empty] | 12×2.5
[26 empty] | Class 2 Conductor | 71221621205 |  |  |  | 24.7 | 1170.4 | [8 empty] | 0.53 | 1.2 | 18.6 | 1.25 | 1.8 | [23 empty] | 16×2.5
[26 empty] | Class 2 Conductor | 71122021205 |  |  |  | 27 | 1376.2 | [8 empty] | 0.53 | 1.2 | 20.8 | 1.25 | 1.9 | [23 empty] | 20×2.5
[26 empty] | Class 2 Conductor | 71122421205 |  |  |  | 29.4 | 1587.1 | [8 empty] | 0.53 | 1.2 | 23.1 | 1.25 | 1.9 | [23 empty] | 24×2.5