## Sheet1
Link | Title | Images |  | Conductor | Insulation | Core Color | Outer Sheath | ('PartNumber', 'PartNumber') | ('Nominal Cross Sectional Area(Sq. mm)', 'Nominal Cross Sectional Area(Sq. mm)') | ('Minimum No. of Strands in Conductor', 'AL') | ('Minimum No. of Strands in Conductor', 'CU') | ('Nominal Thickness of Insulation (mm)', 'Nominal Thickness of Insulation (mm)') | ('Nominal Thickness of Outer Sheath (mm)', 'Nominal Thickness of Outer Sheath (mm)') | ('Approx.Overall Diameter(mm)', 'Approx.Overall Diameter(mm)') | ('Approx. Net Wt.of Cable (Kg/Km)', 'AL CableAYY') | ('Approx. Net Wt.of Cable (Kg/Km)', 'CU CableYY') | Inner Sheath | ('Minimum Thickness of Inner Sheath (mm)', 'Minimum Thickness of Inner Sheath (mm)') | ('Nominal Cross Sectional Area (Sq. mm)', 'Nominal Cross Sectional Area (Sq. mm)') | ('Minimum Thickness of Inner Sheath(mm)', 'Minimum Thickness of Inner Sheath(mm)') | ('Nominal Thickness of Outer Sheath(mm)', 'Nominal Thickness of Outer Sheath(mm)') | ('Approx. Overall Diameter(mm)', 'Approx. Overall Diameter(mm)') | ('Approx. Net Wt.of Cable (kg/km)', 'AL CableAYY') | ('Approx. Net Wt.of Cable (kg/km)', 'CU CableYY') | Neutral Core Color : Black | Armouring | Outer Sheath: | ('PartNumber', 'PartNumber', 'PartNumber') | ('Nominal Cross Sectional Area (Sq. mm)', 'Nominal Cross Sectional Area (Sq. mm)', 'Nominal Cross Sectional Area (Sq. mm)') | ('Minimum No. of Strands in Conductor', 'AL', 'AL') | ('Minimum No. of Strands in Conductor', 'CU', 'CU') | ('Nominal Thickness of Insulation (mm)', 'Nominal Thickness of Insulation (mm)', 'Nominal Thickness of Insulation (mm)') | ('Armouring with Flat AL Strip (AYFaY/YFaY)', 'Nominal Thick. of Arm. Strip (mm)', 'Nominal Thick. of Arm. Strip (mm)') | ('Armouring with Flat AL Strip (AYFaY/YFaY)', 'Minimum Thick. of Out. Sheath(mm)', 'Minimum Thick. of Out. Sheath(mm)') | ('Armouring with Flat AL Strip (AYFaY/YFaY)', 'Approx. Overall Dia.(mm)', 'Approx. Overall Dia.(mm)') | ('Armouring with Flat AL Strip (AYFaY/YFaY)', 'Approx Net Wtof Cable (kg/km)', 'AL Cable AYFaY') | ('Armouring with Flat AL Strip (AYFaY/YFaY)', 'Approx Net Wtof Cable (kg/km)', 'CU Cable YFaY') | ('Armouring with Round Wire (AYWaY/YWaY)', 'Nominal Diameter of Wire (mm)', 'Nominal Diameter of Wire (mm)') | ('Armouring with Round Wire (AYWaY/YWaY)', 'Minimum Thick. of Out. Sheath (mm)', 'Minimum Thick. of Out. Sheath (mm)') | ('Armouring with Round Wire (AYWaY/YWaY)', 'Approx. Overall Dia. (mm)', 'Approx. Overall Dia. (mm)') | ('Armouring with Round Wire (AYWaY/YWaY)', 'Approx Net Wtof Cable (kg/km)', 'AL Cable AYWaY') | ('Armouring with Round Wire (AYWaY/YWaY)', 'Approx Net Wtof Cable (kg/km)', 'CU Cable YWaY') | ('Part Number', 'Part Number', 'Part Number') | ('Nominal Cross Sectional Area(Sq. mm)', 'Nominal Cross Sectional Area(Sq. mm)', 'Nominal Cross Sectional Area(Sq. mm)') | ('Max. DC Conductor Resistance at20°C (Ω/km)', 'Max. DC Conductor Resistance at20°C (Ω/km)', 'AL') | ('Max. DC Conductor Resistance at20°C (Ω/km)', 'Max. DC Conductor Resistance at20°C (Ω/km)', 'CU') | ('Max. AC Conductor Resistance at70°C (Ω/km)', 'Max. AC Conductor Resistance at70°C (Ω/km)', 'AL') | ('Max. AC Conductor Resistance at70°C (Ω/km)', 'Max. AC Conductor Resistance at70°C (Ω/km)', 'CU') | ('Approx.Capacitance of Cable (microF/KM)', 'Approx.Capacitance of Cable (microF/KM)', 'Approx.Capacitance of Cable (microF/KM)') | ('Approx. Capacitance of Cable (microF/KM', 'Approx. Capacitance of Cable (microF/KM', 'Approx. Capacitance of Cable (microF/KM') | ('Normal Current Rating (Amps)', 'With AL Cond.', 'Ground') | ('Normal Current Rating (Amps)', 'With AL Cond.', 'Duct') | ('Normal Current Rating (Amps)', 'With AL Cond.', 'Air') | ('Normal Current Rating (Amps)', 'With CU Cond.', 'Ground') | ('Normal Current Rating (Amps)', 'With CU Cond.', 'Duct') | ('Normal Current Rating (Amps)', 'With CU Cond.', 'Air') | ('Short CircuitCurrent Ratingfor 1sec. Duration(K.Amps)', 'Short CircuitCurrent Ratingfor 1sec. Duration(K.Amps)', 'AL') | ('Short CircuitCurrent Ratingfor 1sec. Duration(K.Amps)', 'Short CircuitCurrent Ratingfor 1sec. Duration(K.Amps)', 'CU') | Cable Design Parameters | ('Minimum Thick. of Inner Sheath (mm)', 'Minimum Thick. of Inner Sheath (mm)', 'Minimum Thick. of Inner Sheath (mm)') | Phase Core Color | Neutral Core Color | Insulation Material | Core Colours | ('No.of Cores', 'No.of Cores') | ('Armouring with Flat AL Strip (AYFaY/YFaY)', 'Nominal Thick. of Arm. Strip (mm)') | ('Armouring with Flat AL Strip (AYFaY/YFaY)', 'Approx. Overall Dia. (mm)') | ('Armouring with Flat AL Strip (AYFaY/YFaY)', 'Approx. Net Wt.of Cable(kg/km)') | ('Armouring with Round Wire (AYWaY/YWaY)', 'Nominal Thickness of Stripfor Arm.(mm)') | ('Armouring with Round Wire (AYWaY/YWaY)', 'Minimum Thick. of Out. Sheath (mm)') | ('Armouring with Round Wire (AYWaY/YWaY)', 'Approx. Overall Dia. (mm)') | ('Armouring with Round Wire (AYWaY/YWaY)', 'Approx Net Wtof Cable (kg/km)') | ('Armoured With Round Wire (YWY)', 'Nominal Thickness of Stripfor Arm. (mm)') | ('Armoured With Round Wire (YWY)', 'Minimum Thickness of Outer Sheath (mm)') | ('Armoured With Round Wire (YWY)', 'Approx. Overall Dia. (mm)') | ('Armoured With Round Wire (YWY)', 'Approx. Net Wt. (kg/km)') | ('Part Number', 'Part Number') | ('Nominal Thickness of Insulation(mm)', 'Nominal Thickness of Insulation(mm)') | ('Nominal Thicknessof Outer Sheath(mm)', 'Nominal Thicknessof Outer Sheath(mm)') | ('Approx. Net Wt. of Cable (kg/km)', 'AL Cable A2XY') | ('Approx. Net Wt. of Cable (kg/km)', 'CU Cable 2XY') | IS: | ('Nominal Thicknessof Outer Sheath (mm)', 'Nominal Thicknessof Outer Sheath (mm)') | ('Approx.Overall Diameter (mm)', 'Approx.Overall Diameter (mm)') | ('Nominal Thickness of Insulation(mm)', 'Nominal Thickness of Insulation(mm)', 'Nominal Thickness of Insulation(mm)') | ('Armouring with flat strip (A2XFaY/ 2XFaY)', 'Nominal Thickness of Arm. Strip(mm)', 'Nominal Thickness of Arm. Strip(mm)') | ('Armouring with flat strip (A2XFaY/ 2XFaY)', 'MinimumThickness of Outer Sheath(mm)', 'MinimumThickness of Outer Sheath(mm)') | ('Armouring with flat strip (A2XFaY/ 2XFaY)', 'Approx. Overall Dia.(mm)', 'Approx. Overall Dia.(mm)') | ('Armouring with flat strip (A2XFaY/ 2XFaY)', 'Approx Net Wt.of Cable (kg/km)', 'AL Cable A2XFaY') | ('Armouring with flat strip (A2XFaY/ 2XFaY)', 'Approx Net Wt.of Cable (kg/km)', 'CU Cable 2XFaY') | ('Armouring with Round Wire (AYWaY/YWaY)', 'Nominal Diameter of Wire(mm)', 'Nominal Diameter of Wire(mm)') | ('Armouring with Round Wire (AYWaY/YWaY)', 'Minimum Thickness of Outer Sheath(mm)', 'Minimum Thickness of Outer Sheath(mm)') | ('Armouring with Round Wire (AYWaY/YWaY)', 'Approx. Overall Dia.(mm)', 'Approx. Overall Dia.(mm)') | ('Armouring with Round Wire (AYWaY/YWaY)', 'Approx Net Wt.of Cable (kg/km)', 'AL Cable AYWaY') | ('Armouring with Round Wire (AYWaY/YWaY)', 'Approx Net Wt.of Cable (kg/km)', 'CU Cable YWaY') | ('Minimum Thickness of Inner Sheath(mm)', 'Minimum Thickness of Inner Sheath(mm)', 'Minimum Thickness of Inner Sheath(mm)') | ('Size Cores x Sq. mm +Neutral(Sq. mm)', 'Size Cores x Sq. mm +Neutral(Sq. mm)', 'Size Cores x Sq. mm +Neutral(Sq. mm)') | ('Armouring with flat strip (A2XFY/ 2XFY)', 'Nominal Thickness of Arm.Strip(mm)', 'Nominal Thickness of Arm.Strip(mm)') | ('Armouring with flat strip (A2XFY/ 2XFY)', 'Minimum Thickness of OuterSheath(mm)', 'Minimum Thickness of OuterSheath(mm)') | ('Armouring with flat strip (A2XFY/ 2XFY)', 'Approx.OverallDia.(mm)', 'Approx.OverallDia.(mm)') | ('Armouring with flat strip (A2XFY/ 2XFY)', 'Approx. Net Wt.of Cable (kg/km)', 'AL Cable A2XFY') | ('Armouring with flat strip (A2XFY/ 2XFY)', 'Approx. Net Wt.of Cable (kg/km)', 'CU Cable2XFY') | ('Armouring with round wire (A2XWY/ 2XWY)', 'Nominal Diameter of Wire(mm)', 'Nominal Diameter of Wire(mm)') | ('Armouring with round wire (A2XWY/ 2XWY)', 'Minimum Thickness of OuterSheath (mm)', 'Minimum Thickness of OuterSheath (mm)') | ('Armouring with round wire (A2XWY/ 2XWY)', 'Approx. Overall Dia.(mm)', 'Approx. Overall Dia.(mm)') | ('Armouring with round wire (A2XWY/ 2XWY)', 'Approx. Net Wt.of Cable (kg/km)', 'AL Cable A2XFY') | ('Armouring with round wire (A2XWY/ 2XWY)', 'Approx. Net Wt.of Cable (kg/km)', 'CU Cable 2XWY') | ('No. of Cores', 'No. of Cores', 'No. of Cores') | ('Unarmoured (2XY)', 'Nominal Thickness of Outer Sheath(mm)', 'Nominal Thickness of Outer Sheath(mm)') | ('Unarmoured (2XY)', 'Approx. Overall Dia.(mm)', 'Approx. Overall Dia.(mm)') | ('Unarmoured (2XY)', 'Approx. Net Wt.of Cable(kg/km)', 'Approx. Net Wt.of Cable(kg/km)') | ('Armoured With Flat Strips (2XFY)', 'NominalThicknessof Arm.Strip(mm)', 'NominalThicknessof Arm.Strip(mm)') | ('Armoured With Flat Strips (2XFY)', 'MinimumThicknessof OuterSheath(mm)', 'MinimumThicknessof OuterSheath(mm)') | ('Armoured With Flat Strips (2XFY)', 'Approx. Overall Dia.(mm)', 'Approx. Overall Dia.(mm)') | ('Armoured With Flat Strips (2XFY)', 'Approx.Net Wt.of Cable(kg/km)', 'Approx.Net Wt.of Cable(kg/km)') | ('Armoured With Round Wire (2XWY)', 'Nominal Thickness of Arm.Strip(mm)', 'Nominal Thickness of Arm.Strip(mm)') | ('Armoured With Round Wire (2XWY)', 'Minimum Thickness of OuterSheath(mm)', 'Minimum Thickness of OuterSheath(mm)') | ('Armoured With Round Wire (2XWY)', 'App.Overall Dia.(mm )', 'App.Overall Dia.(mm )') | ('Armoured With Round Wire (2XWY)', 'Approx.Net Wt.of Cable(kg/km)', 'Approx.Net Wt.of Cable(kg/km)') | Application | Temperature Range | Nominal Voltage | Test Voltage | Max. permissible tensile stress with cable grip for CU-conductor | J-type | O-type | Properties | PartNumber | No. of Cores and Nominal Cross-Section Area(Sq. mm) | Approx. Cable Diameter(mm) | Approx. Copper Weight(kg/km) | Approx.Weight Cable(kg/km) | Standard | Voltage Rating | Minimum Bending Radius | Core colours: | Note | ('Unnamed: 0_level_0', 'Unnamed: 0_level_1') | ('Insulation Thickness(mm)', 'Insulation Thickness(mm)') | ('Armour Wire Diameter(mm)', 'Armour Wire Diameter(mm)') | ('Approx. Dia. under Armour(mm)', 'Approx. Dia. under Armour(mm)') | ('Approx Overall Diameter(mm)', 'Approx Overall Diameter(mm)') | ('Approx Cable Weight(kg/km)', 'Approx Cable Weight(kg/km)') | ('Maximum Resistance of Cable', 'DC at 20°C(Ω/km)') | ('Maximum Resistance of Cable', 'AC at 90°C(Ω/km)') | ('Reactance at 50 Hz(Ω/km)', 'Reactance at 50 Hz(Ω/km)') | ('Impedance AC at90°C(Ω/km)', 'Impedance AC at90°C(Ω/km)') | ('Star Capacitance(μF/km)', 'Star Capacitance(μF/km)') | ('MaximumArmourResistance(Ω/km)', 'MaximumArmourResistance(Ω/km)') | Conductor : | Insulation : | Core colours : | 3C - | 4C - | Inner sheath : | Outer sheath : | Cable Construction | ('No. of Cores and Nominal Cross Sectional Area (Sq. mm)', 'No. of Cores and Nominal Cross Sectional Area (Sq. mm)') | ('Nom. Insulation Thickness (mm)', 'Nom. Insulation Thickness (mm)') | ('Nom. Bedding Thickness (mm)', 'Nom. Bedding Thickness (mm)') | ('Nom. Outer sheath Thickness (mm)', 'Nom. Outer sheath Thickness (mm)') | ('Approx. Overall Dia. (mm)', 'Approx. Overall Dia. (mm)') | ('Approx. Cable Weight (kg/km)', 'Approx. Cable Weight (kg/km)') | ('Current Carrying Capacity (Amp.)', 'In Ground at 30°C') | ('Current Carrying Capacity (Amp.)', 'In Air at 40°C') | Temperature Range :
https://www.rrkabel.com/power-cables/power-cables-ayyyy-1-core | AYY/YY-1 CORE | ['https://www.rrkabel.com/Uploads/Products/102/ProductZoomForMoreDetailsImage/copper-AYY-YY-1-Core.jpg', 'https://www.rrkabel.com/Uploads/Products/102/ProductZoomImage/03-.jpg', 'https://www.rrkabel.com/Uploads/Products/304/ProductFeaturesDetails/01.png', 'https://www.rrkabel.com/Uploads/Products/304/ProductFeaturesDetails/01.png'] | ['1.1 kV (A.C) & 1.5 kV (D.C ) to Earth', '1 cores AL / CU conductor, PVC insulated, unarmoured cables as per IS 1554 Part - 1.'] | ['AL up to 10 Sq. mm conductor are solid Cl.1 as per IS 8130. And above 10 Sq. mm conductor are stranded round or compact Cl. 2 as per IS 8130', 'In CU 4 & 6 Sq. mm conductor are solid Cl.1 or stranded Cl. 2 as per IS 8130. 10 Sq. mm & above stranded round or stranded compact Cl. 2 as per IS 8130'] | ['PVC Type - A, as per IS 5831. (Option : HR PVC Type - C, as per IS 5831)'] | ['Red or yellow or blue or black or natural'] | ['PVC Type ST-1 as per IS 5831. (Option : PVC Type - ST 2 as per IS 5831 / FR Type / FRLS Type )']
[8 empty] | 110100100016 | 16 | 6 | 6 | 1 | 1.8 | 11 | 160 | 260
[8 empty] | 110100100025 | 25 | 6 | 6 | 1.2 | 1.8 | 13 | 210 | 365
[8 empty] | 110100100035 | 35 | 6 | 6 | 1.2 | 1.8 | 14 | 250 | 460
[8 empty] | 110100100050 | 50 | 6 | 6 | 1.4 | 1.8 | 16 | 300 | 610
[8 empty] | 110100100070 | 70 | 12 | 12 | 1.4 | 1.8 | 17 | 400 | 830
[8 empty] | 110100100095 | 95 | 15 | 15 | 1.6 | 1.8 | 19 | 500 | 1100
[8 empty] | 110100100120 | 120 | 15 | 18 | 1.6 | 2 | 21 | 600 | 1350
[8 empty] | 110100100150 | 150 | 15 | 18 | 1.8 | 2 | 23 | 750 | 1680
[8 empty] | 110100100185 | 185 | 30 | 30 | 2 | 2 | 25 | 900 | 2050
[8 empty] | 110100100240 | 240 | 30 | 34 | 2.2 | 2 | 28 | 1100 | 2600
[8 empty] | 110100100300 | 300 | 30 | 34 | 2.4 | 2 | 30 | 1350 | 3200
[8 empty] | 110100100400 | 400 | 53 | 53 | 2.6 | 2.2 | 35 | 1700 | 4200
[8 empty] | 110100100500 | 500 | 53 | 53 | 3 | 2.2 | 38 | 2150 | 5250
[8 empty] | 110100100630 | 630 | 53 | 53 | 3.4 | 2.4 | 43 | 2750 | 6650
[8 empty] | 110100100800 | 800 | 53 | 53 | 3.4 | 2.4 | 48 | 3300 | 8250
[8 empty] | 110100101000 | 1000 | 53 | 53 | 3.4 | 2.6 | 52 | 4100 | 10300
https://www.rrkabel.com/power-cables/power-cables-ayyyy-2-core | AYY/YY-2 CORE | ['https://www.rrkabel.com/Uploads/Products/103/ProductZoomForMoreDetailsImage/aluminium-AYY-YY-2-Core.jpg', 'https://www.rrkabel.com/Uploads/Products/103/ProductZoomImage/03-.jpg', 'https://www.rrkabel.com/Uploads/Products/307/ProductFeaturesDetails/01.png', 'https://www.rrkabel.com/Uploads/Products/307/ProductFeaturesDetails/01.png'] | ['1.1 kV (A.C) & 1.5 kV (D.C ) to Earth', '2 cores AL / CU conductor, PVC insulated, unarmoured cables as per IS 1554 Part - 1.'] | ['AL up to 10 Sq. mm conductor are solid Cl. 1 as per IS 8130. And above 10 Sq. mm conductor are stranded round or compact round or Compact shape conductor Cl. 2 as per IS 8130', 'In CU 4 & 6 Sq. mm conductor are solid Cl. 1 or stranded round Cl. 2 as per IS 8130. 10 Sq. mm conductor is stranded round or stranded compact conductor Cl. 2 as per IS 8130', 'Above 10 Sq. mm conductor are stranded round or compact round or compacted shaped Cl. 2 as per IS 8130'] | ['PVC Type - A, as per IS 5831.(Option : HR PVC Type - C, as per IS 5831)'] | ['Red, black'] | ['PVC Type ST - 1 as per IS 5831 (Option : PVC Type - ST - 2 as per IS 5831 / FR Type / FRLS Type)'] | [9 empty] | ['PVC / PVC tape as per IS 1554 (P - 1)']
[8 empty] | 110200200004 | 4 | _ | 1/7 | 1 | 1.8 | 14 | 240 | 290 |  | 0.3
[8 empty] | 110200200006 | 6 | 1 | 1/7 | 1 | 1.8 | 17 | 300 | 370 |  | 0.3
[8 empty] | 110200200010 | 10 | 1 | 6 | 1 | 1.8 | 18 | 400 | 520 |  | 0.3
[8 empty] | 110200200016 | 16 | 6 | 6 | 1 | 1.8 | 17 | 430 | 630 |  | 0.3
[8 empty] | 110200200025 | 25 | 6 | 6 | 1.2 | 2 | 19 | 450 | 750 |  | 0.3
[8 empty] | 110200200035 | 35 | 6 | 6 | 1.2 | 2 | 21 | 550 | 980 |  | 0.3
[8 empty] | 110200200050 | 50 | 6 | 6 | 1.4 | 2 | 24 | 700 | 1300 |  | 0.3
[8 empty] | 110200200070 | 70 | 12 | 12 | 1.4 | 2 | 26 | 850 | 1700 |  | 0.3
[8 empty] | 110200200095 | 95 | 15 | 15 | 1.6 | 2.2 | 30 | 1150 | 2300 |  | 0.4
[8 empty] | 110200200120 | 120 | 15 | 18 | 1.6 | 2.2 | 32 | 1300 | 2800 |  | 0.4
[8 empty] | 110200200150 | 150 | 15 | 18 | 1.8 | 2.4 | 34 | 1600 | 3450 |  | 0.4
[8 empty] | 110200200185 | 185 | 30 | 30 | 2 | 2.4 | 38 | 2000 | 4300 |  | 0.5
[8 empty] | 110200200240 | 240 | 30 | 34 | 2.2 | 2.6 | 42 | 2500 | 5500 |  | 0.5
[8 empty] | 110200200300 | 300 | 30 | 34 | 2.4 | 2.8 | 46 | 3000 | 6700 |  | 0.6
[8 empty] | 110200200400 | 400 | 53 | 53 | 2.6 | 3.2 | 52 | 3800 | 8750 |  | 0.7
[8 empty] | 110200200500 | 500 | 53 | 53 | 3 | 3.4 | 54 | 4800 | 11000 |  | 0.7
[8 empty] | 110200200630 | 630 | 53 | 53 | 3.4 | 3.8 | 65 | 6000 | 13800 |  | 0.7
https://www.rrkabel.com/power-cables/power-cables-ayyyy-3-core | AYY/YY-3 CORE | ['https://www.rrkabel.com/Uploads/Products/104/ProductZoomForMoreDetailsImage/copper-AYY-YY-3-Core.jpg', 'https://www.rrkabel.com/Uploads/Products/104/ProductZoomImage/03-.jpg', 'https://www.rrkabel.com/Uploads/Products/310/ProductFeaturesDetails/01.png', 'https://www.rrkabel.com/Uploads/Products/310/ProductFeaturesDetails/01.png'] | ['1.1 kV (A.C) & 1.5 kV (D.C ) to Earth', '3 cores AL / CU conductor, PVC insulated, unarmoured cables as per IS 1554 Part - 1.'] | ['AL up to 10 Sq. mm conductor are solid Cl. 1 as per IS 8130. And above 10 Sq. mm conductor are stranded compacted shape Cl. 2 as per IS 8130', 'In CU 4 & 6 Sq. mm conductor are solid Cl. 1 or stranded Cl. 2 as per IS 8130. 10 Sq. mm conductor is stranded Cl. 2 round as per IS 8130. Above 10 Sq. mm conductor are stranded compacted shaped Cl. 2 as per IS 8130'] | ['PVC Type - A, as per IS 5831.(Option : HR PVC Type - C, as per IS 5831)'] | ['Red, yellow, blue'] | ['PVC Type ST - 1 as per IS 5831 (Option : PVC Type - ST - 2 as per IS 5831, FR Type / FRLS Type)'] | [9 empty] | ['PVC / PVC tape as per IS 1554 (P - 1)']
[8 empty] | 110300300004 |  | _ | 1/7 | 1 | [6 empty] | 4 | 0.3 | 1.8 | 16 | 280 | 330
[8 empty] | 110300300006 |  | 1 | 1/7 | 1 | [6 empty] | 6 | 0.3 | 1.8 | 18 | 350 | 460
[8 empty] | 110300300010 |  | 1 | 6 | 1 | [6 empty] | 10 | 0.3 | 1.8 | 19 | 430 | 640
[8 empty] | 110300300016 |  | 6 | 6 | 1 | [6 empty] | 16 | 0.3 | 1.8 | 19 | 450 | 720
[8 empty] | 110300300025 |  | 6 | 6 | 1.2 | [6 empty] | 25 | 0.3 | 2 | 22 | 610 | 1070
[8 empty] | 110300300035 |  | 6 | 6 | 1.2 | [6 empty] | 35 | 0.3 | 2 | 24 | 730 | 1390
[8 empty] | 110300300050 |  | 6 | 6 | 1.4 | [6 empty] | 50 | 0.3 | 2 | 27 | 930 | 1860
[8 empty] | 110300300070 |  | 12 | 12 | 1.4 | [6 empty] | 70 | 0.4 | 2.2 | 30 | 1190 | 2490
[8 empty] | 110300300095 |  | 15 | 15 | 1.6 | [6 empty] | 95 | 0.4 | 2.2 | 34 | 1590 | 3340
[8 empty] | 110300300120 |  | 15 | 18 | 1.6 | [6 empty] | 120 | 0.4 | 2.2 | 37 | 1890 | 4090
[8 empty] | 110300300150 |  | 15 | 18 | 1.8 | [6 empty] | 150 | 0.5 | 2.4 | 40 | 2290 | 5090
[8 empty] | 110300300185 |  | 30 | 30 | 2 | [6 empty] | 185 | 0.5 | 2.6 | 44 | 2740 | 6190
[8 empty] | 110300300240 |  | 30 | 34 | 2.2 | [6 empty] | 240 | 0.6 | 2.8 | 50 | 3490 | 7940
[8 empty] | 110300300300 |  | 30 | 34 | 2.4 | [6 empty] | 300 | 0.6 | 3 | 55 | 4290 | 9890
[8 empty] | 110300300400 |  | 53 | 53 | 2.6 | [6 empty] | 400 | 0.7 | 3.4 | 62 | 5430 | 12790
[8 empty] | 110300300500 |  | 53 | 53 | 3 | [6 empty] | 500 | 0.7 | 3.6 | 69 | 6900 | 16190
[8 empty] | 110300300630 |  | 53 | 53 | 3.4 | [6 empty] | 630 | 0.7 | 4 | 77 | 8690 | 20390
https://www.rrkabel.com/power-cables/power-cables-ayyyy-3-5-core | AYY/YY-3.5 CORE | ['https://www.rrkabel.com/Uploads/Products/105/ProductZoomForMoreDetailsImage/aluminium-AYY-YY-3.5-Core.jpg', 'https://www.rrkabel.com/Uploads/Products/105/ProductZoomImage/03-.jpg', 'https://www.rrkabel.com/Uploads/Products/313/ProductFeaturesDetails/01.png', 'https://www.rrkabel.com/Uploads/Products/313/ProductFeaturesDetails/01.png'] | ['1.1 kV (A.C) & 1.5 kV (D.C ) to Earth', '3.5 cores AL / CU conductor, PVC insulated, unarmoured cables as per IS 1554 Part-1. Conductor : AL / CU stranded compact shaped conductor as per Cl. 2, IS 8130 Insulation : PVC Type - A as per IS 5831. (Option : HR PVC Type - C, as per IS 5831) Phase Core Color : Red, yellow, blue'] |  |  |  | ['PVC Type ST - 1 as per IS 5831 (Option : PVC Type ST - 2 as per IS 5831 / FR Type / FRLS Type)'] | [9 empty] | ['PVC / PVC tape as per IS 1554 (P - 1)'] | [7 empty] | []
[8 empty] | 110401010211 |  | 6/6 | 6/6 | 1.2/1.0 | [6 empty] | 3×25+16 | 0.3 | 2 | 24 | 680 | 1250
[8 empty] | 110401020211 |  | 6/6 | 6/6 | 1.2/1.0 | [6 empty] | 3×35+16 | 0.3 | 2 | 26 | 830 | 1585
[8 empty] | 110401030211 |  | 6/6 | 6/6 | 1.4/1.2 | [6 empty] | 3×50+25 | 0.3 | 2 | 29 | 1030 | 2080
[8 empty] | 110401040211 |  | 12/6 | 12/6 | 1.4/1.2 | [6 empty] | 3×70+35 | 0.4 | 2.2 | 32 | 1380 | 2880
[8 empty] | 110401050211 |  | 15/6 | 15/6 | 1.6/1.4 | [6 empty] | 3×95+50 | 0.4 | 2.2 | 36 | 1785 | 3885
[8 empty] | 110401060211 |  | 15/12 | 18/12 | 1.6/1.4 | [6 empty] | 3×120+70 | 0.5 | 2.4 | 40 | 2190 | 4830
[8 empty] | 110401070211 |  | 15/12 | 18/12 | 1.8/1.4 | [6 empty] | 3×150+70 | 0.5 | 2.4 | 44 | 2580 | 5780
[8 empty] | 110401080211 |  | 30/15 | 30/15 | 2.0/1.6 | [6 empty] | 3×185+95 | 0.5 | 2.6 | 48 | 3185 | 7180
[8 empty] | 110401090211 |  | 30/15 | 34/18 | 2.2/1.6 | [6 empty] | 3×240+120 | 0.6 | 3 | 54 | 4085 | 9280
[8 empty] | 110401100211 |  | 30/15 | 34/18 | 2.4/1.8 | [6 empty] | 3×300+150 | 0.6 | 3.2 | 62 | 4980 | 11480
[8 empty] | 110401110211 |  | 53/30 | 53/30 | 2.6/2.0 | [6 empty] | 3×400+185 | 0.7 | 3.4 | 68 | 6280 | 14985
[8 empty] | 110401120211 |  | 53/30 | 53/34 | 3.0/2.2 | [6 empty] | 3×500+240 | 0.7 | 3.8 | 77 | 7985 | 18480
[8 empty] | 110401130211 |  | 53/30 | 53/34 | 3.4/2.4 | [6 empty] | 3×630+300 | 0.7 | 4 | 87 | 9980 | 23485
https://www.rrkabel.com/power-cables/power-cables-ayyyy-4-core | AYY/YY-4 CORE | ['https://www.rrkabel.com/Uploads/Products/106/ProductZoomForMoreDetailsImage/copper-AYY-YY-4-Core.jpg', 'https://www.rrkabel.com/Uploads/Products/106/ProductZoomImage/03-.jpg', 'https://www.rrkabel.com/Uploads/Products/316/ProductFeaturesDetails/01.png', 'https://www.rrkabel.com/Uploads/Products/316/ProductFeaturesDetails/01.png'] | ['1.1 kV (A.C) & 1.5 kV (D.C ) to Earth', '4 cores AL / CU conductor, PVC insulated, unarmoured cables as per IS 1554 Part - 1.'] | ['AL up to 10 Sq. mm conductor are solid Cl. 1 as per IS 8130. And above 10 Sq. mm conductor are stranded compacted shape Cl. 2 as per IS 8130', 'In CU 4 & 6 Sq. mm conductor are solid Cl. 1 or stranded Cl. 2 as per IS 8130. 10 Sq. mm conductor is stranded Cl. 2 round as per IS 8130. Above 10 Sq. mm conductor are stranded compacted shaped Cl. 2 as per IS 8130'] | ['PVC Type - A, as per IS 5831. (Option : HR PVC Type - C, as per IS 5831)'] | ['Red, yellow, blue, black'] | ['PVC Type ST - 1 as per IS 5831 (Option : PVC Type - ST - 2 as per IS 5831, FR Type / FRLS Type)'] | [9 empty] | ['PVC/PVC tape as per IS 1554 (P-1)']
[8 empty] | 110500400004 |  | _ | 1/7 | 1 | [6 empty] | 4 | 0.3 | 1.8 | 16 | 290 | 390
[8 empty] | 110500400006 |  | 1 | 1/7 | 1 | [6 empty] | 6 | 0.3 | 1.8 | 18 | 380 | 530
[8 empty] | 110500400010 |  | 1 | 6 | 1 | [6 empty] | 10 | 0.3 | 1.8 | 20 | 530 | 770
[8 empty] | 110500400016 |  | 6 | 6 | 1 | [6 empty] | 16 | 0.3 | 2 | 23 | 550 | 940
[8 empty] | 110500400025 |  | 6 | 6 | 1.2 | [6 empty] | 25 | 0.3 | 2 | 26 | 740 | 1350
[8 empty] | 110500400035 |  | 6 | 6 | 1.2 | [6 empty] | 35 | 0.3 | 2 | 30 | 925 | 1785
[8 empty] | 110500400050 |  | 6 | 6 | 1.4 | [6 empty] | 50 | 0.4 | 2.2 | 34 | 1230 | 2480
[8 empty] | 110500400070 |  | 12 | 12 | 1.4 | [6 empty] | 70 | 0.4 | 2.2 | 38 | 1540 | 3285
[8 empty] | 110500400095 |  | 15 | 15 | 1.6 | [6 empty] | 95 | 0.4 | 2.4 | 43 | 2030 | 4385
[8 empty] | 110500400120 |  | 15 | 18 | 1.6 | [6 empty] | 120 | 0.5 | 2.4 | 46 | 2385 | 5360
[8 empty] | 110500400150 |  | 15 | 18 | 1.8 | [6 empty] | 150 | 0.5 | 2.6 | 51 | 2925 | 6650
[8 empty] | 110500400185 |  | 30 | 30 | 2 | [6 empty] | 185 | 0.6 | 2.8 | 55 | 3630 | 8230
[8 empty] | 110500400240 |  | 30 | 34 | 2.2 | [6 empty] | 240 | 0.6 | 3 | 60 | 4580 | 10530
[8 empty] | 110500400300 |  | 30 | 34 | 2.4 | [6 empty] | 300 | 0.7 | 3.4 | 66 | 5480 | 12950
[8 empty] | 110500400400 |  | 53 | 53 | 2.6 | [6 empty] | 400 | 0.7 | 3.6 | 73 | 6780 | 16700
[8 empty] | 110500400500 |  | 53 | 53 | 3 | [6 empty] | 500 | 0.7 | 4 | 82 | 8580 | 20980
[8 empty] | 110500400630 |  | 53 | 53 | 3.4 | [6 empty] | 630 | 0.7 | 4 | 92 | 10980 | 25980
https://www.rrkabel.com/power-cables/power-cables-ayfayyfay-aywayyway | AYFaY/YFaY-AYWaY/YWaY | ['https://www.rrkabel.com/Uploads/Products/107/ProductZoomForMoreDetailsImage/aluminium-AYFaY-YFaY-AYWaY-YWaY.jpg', 'https://www.rrkabel.com/Uploads/Products/107/ProductZoomImage/03-.jpg', 'https://www.rrkabel.com/Uploads/Products/319/ProductFeaturesDetails/01.png', 'https://www.rrkabel.com/Uploads/Products/319/ProductFeaturesDetails/01.png'] | ['1.1 kV (A.C) & 1.5 kV (D.C ) to Earth', '1 cores AL / CU conductor, PVC insulated, aluminum steel strip / wire armoured cables as per IS 1554 Part - 1.'] | ['AL up to 10 Sq. mm conductor are solid Cl. 1 as per IS 8130. And above 10 Sq. mm conductor are stranded round or compact Cl. 2 as per IS 8130', 'In CU 4 & 6 Sq. mm conductor are solid Cl. 1 or stranded Cl. 2 as per IS 8130. 10 Sq. mm & above stranded round or stranded compact Cl. 2 as per IS 8130'] | ['PVC Type - A, as per IS 5831.( Option : HR PVC Type - C, as per IS 5831)'] | ['Red or yellow or blue or black or natural'] | [19 empty] | ['Single armouring of aluminium wire or aluminum strip as per IS 1554 P - 1'] | ['PVC Type ST - 1 as per IS 5831 (Option : PVC Type ST - 2 as per IS 5831 / FR Type / FRLS Type)']
[28 empty] | 110600100016 | 16 | 6 | 6 | 1.3 | [5 empty] | 1.4 | 1.24 | 14 | 250 | 350
[28 empty] | 110600100025 | 25 | 6 | 6 | 1.5 | [5 empty] | 1.4 | 1.24 | 15 | 300 | 450
[28 empty] | 110600100035 | 35 | 6 | 6 | 1.5 | [5 empty] | 1.4 | 1.24 | 16 | 350 | 560
[28 empty] | 110600100050 | 50 | 6 | 6 | 1.7 | [5 empty] | 1.4 | 1.24 | 18 | 450 | 750
[28 empty] | 110600100070 | 70 | 12 | 12 | 1.7 | [5 empty] | 1.4 | 1.4 | 20 | 550 | 980
[28 empty] | 110600100095 | 95 | 15 | 15 | 1.9 | 0.8 | 1.4 | 21 | 650 | 1230 | 1.6 | 1.4 | 22 | 700 | 1300
[28 empty] | 110600100120 | 120 | 15 | 18 | 1.9 | 0.8 | 1.4 | 23 | 750 | 1500 | 1.6 | 1.4 | 24 | 800 | 1550
[28 empty] | 110600100150 | 150 | 15 | 18 | 2.1 | 0.8 | 1.4 | 24 | 900 | 1830 | 1.6 | 1.4 | 26 | 950 | 1880
[28 empty] | 110600100185 | 185 | 30 | 30 | 2.3 | 0.8 | 1.4 | 27 | 1050 | 2200 | 1.6 | 1.4 | 29 | 1100 | 2250
[28 empty] | 110600100240 | 240 | 30 | 34 | 2.5 | 0.8 | 1.4 | 30 | 1300 | 2800 | 1.6 | 1.56 | 32 | 1400 | 2900
[28 empty] | 110600100300 | 300 | 30 | 34 | 2.7 | 0.8 | 1.56 | 32 | 1600 | 3450 | 1.6 | 1.56 | 33 | 1650 | 3500
[28 empty] | 110600100400 | 400 | 53 | 53 | 3 | 0.8 | 1.56 | 37 | 1950 | 4400 | 2 | 1.56 | 39 | 2100 | 4580
[28 empty] | 110600100500 | 500 | 53 | 53 | 3.4 | 0.8 | 1.56 | 40 | 2400 | 5500 | 2 | 1.72 | 42 | 2700 | 5800
[28 empty] | 110600100630 | 630 | 53 | 53 | 3.9 | 0.8 | 1.72 | 45 | 3100 | 7000 | 2 | 1.88 | 48 | 3300 | 7200
[28 empty] | 110600100800 | 800 | 53 | 53 | 3.9 | 0.8 | 1.88 | 49 | 3700 | 8650 | 2 | 1.88 | 52 | 4000 | 8950
[28 empty] | 110600101000 | 1000 | 53 | 53 | 3.9 | 0.8 | 2.04 | 55 | 4600 | 10800 | 2.5 | 2.04 | 59 | 4900 | 11000
[43 empty] | 110600100016 | 16 | 1.91 | 1.15 | 2.29 | 1.38 | 0.128 | 0.81 | 66 | 65 | 64 | 85 | 83 | 82 | 1.22 | 1.84
[43 empty] | 110600100025 | 25 | 1.2 | 0.727 | 1.44 | 0.87 | 0.12 | 0.87 | 86 | 84 | 84 | 110 | 110 | 110 | 1.9 | 2.88
[43 empty] | 110600100035 | 35 | 0.868 | 0.524 | 1.04 | 0.63 | 0.114 | 1 | 100 | 100 | 105 | 130 | 125 | 130 | 2.66 | 4.03
[43 empty] | 110600100050 | 50 | 0.641 | 0.387 | 0.769 | 0.464 | 0.11 | 1.03 | 120 | 115 | 130 | 155 | 150 | 165 | 3.8 | 5.75
[43 empty] | 110600100070 | 70 | 0.443 | 0.268 | 0.532 | 0.322 | 0.103 | 1.21 | 140 | 135 | 155 | 190 | 175 | 205 | 5.32 | 8.05
[43 empty] | 110600100095 | 95 | 0.32 | 0.193 | 0.384 | 0.232 | 0.101 | 1.27 | 175 | 155 | 190 | 220 | 200 | 245 | 7.22 | 10.9
[43 empty] | 110600100120 | 120 | 0.253 | 0.153 | 0.304 | 0.184 | 0.096 | 1.42 | 195 | 170 | 220 | 250 | 220 | 280 | 9.12 | 13.8
[43 empty] | 110600100150 | 150 | 0.206 | 0.124 | 0.247 | 0.1488 | 0.094 | 1.42 | 220 | 190 | 250 | 280 | 245 | 320 | 11.4 | 17.3
[43 empty] | 110600100185 | 185 | 0.164 | 0.0991 | 0.197 | 0.1189 | 0.092 | 1.44 | 240 | 210 | 290 | 305 | 260 | 370 | 14.1 | 21.3
[43 empty] | 110600100240 | 240 | 0.125 | 0.0754 | 0.151 | 0.0912 | 0.09 | 1.53 | 270 | 225 | 335 | 345 | 285 | 425 | 18.2 | 27.6
[43 empty] | 110600100300 | 300 | 0.1 | 0.0601 | 0.122 | 0.0733 | 0.088 | 1.56 | 295 | 245 | 380 | 375 | 310 | 475 | 22.8 | 34.5
[43 empty] | 110600100400 | 400 | 0.0778 | 0.047 | 0.0961 | 0.058 | 0.088 | 1.59 | 325 | 275 | 435 | 400 | 335 | 550 | 30.4 | 46
[43 empty] | 110600100500 | 500 | 0.0605 | 0.0366 | 0.076 | 0.0459 | 0.087 | 1.67 | 345 | 295 | 480 | 425 | 355 | 590 | 38 | 57.5
[43 empty] | 110600100630 | 630 | 0.0469 | 0.0283 | 0.061 | 0.0368 | 0.086 | 1.67 | 390 | 320 | 550 | 470 | 375 | 660 | 47.88 | 72.5
[43 empty] | 110600100800 | 800 | 0.0367 | 0.0221 | 0.0503 | 0.0303 | 0.083 | 1.75 | 450 | 380 | 610 | 530 | 423 | 725 | 60.8 | 92
[43 empty] | 110600101000 | 1000 | 0.0291 | 0.0176 | 0.0422 | 0.0255 | 0.082 | 1.94 | 500 | 414 | 680 | 590 | 471 | 870 | 76 | 115
https://www.rrkabel.com/power-cables/power-cables-ayfyyfy-aywyywy-2-core | AYFY/YFY-AYWY/YWY-2 CORE | ['https://www.rrkabel.com/Uploads/Products/108/ProductZoomForMoreDetailsImage/copper-AYFY-YFY-AYWY-YWY-2-Cores.jpg', 'https://www.rrkabel.com/Uploads/Products/108/ProductZoomImage/last-03.png', 'https://www.rrkabel.com/Uploads/Products/322/ProductFeaturesDetails/01.png', 'https://www.rrkabel.com/Uploads/Products/322/ProductFeaturesDetails/01.png'] | ['1.1 kV (A.C) & 1.5 kV (D.C ) to Earth', '2 cores AL / CU conductor, PVC insulated, galvanised steel strip / wire armoured cables as per IS 1554 Part - 1.'] | ['AL up to 10 Sq. mm conductor are solid Cl. 1 as per IS 8130. And above 10 Sq. mm conductor are stranded round or compact round or compact shape conductor Cl. 2 as per IS 8130', 'In CU 4 & 6 Sq. mm conductor are solid Cl. 1 or stranded round Cl. 2 as per IS 8130. 10 Sq. mm conductor is stranded round or stranded compact conductor Cl. 2 as per IS 8130', 'Above 10 Sq. mm conductor are stranded round or compact round or compacted shaped Cl. 2 as per IS 8130.'] | ['PVC Type - A, as per IS 5831. (Option : HR PVC Type - C, as per IS 5831)'] | ['Red, black'] | ['PVC Type ST - 1 as per IS 5831 (Option : PVC Type ST - 2 as per IS 5831 / FR Type / FRLS Type)'] | [9 empty] | ['PVC / PVC tape as per IS 1554 (P - 1)'] | [8 empty] | ['Single armouring of G.I. Wire or G.I. Strip as per IS 3975'] | [32 empty] | ['While ordering, in addition to the part number the following details shall also be advised: Conductor Type (Aluminium or Copper) and class of conductor (Cl. 1 or 2). Insulation Type – PVC Type A / C. Sheath Type – PVC Type ST – 1 / FR / FRLS; PVC Type ST – 2 / FR /FRLS.']
[28 empty] | 110700200004 | 4 | _ | 1/7 | 1 | [5 empty] | 1.4 | 1.24 | 18 | 600 | 650 | [17 empty] | 0.3
[28 empty] | 110700200006 | 6 | 1 | 1/7 | 1 | [5 empty] | 1.4 | 1.24 | 19 | 660 | 730 | [17 empty] | 0.3
[28 empty] | 110700200010 | 10 | 1 | 6 | 1 | [5 empty] | 1.4 | 1.24 | 20 | 750 | 870 | [17 empty] | 0.3
[28 empty] | 110700200016 | 16 | 6 | 6 | 1 | 0.8 | 1.4 | 18 | 580 | 780 | 1.6 | 1.4 | 20 | 750 | 950 | [17 empty] | 0.3
[28 empty] | 110700200025 | 25 | 6 | 6 | 1.2 | 0.8 | 1.4 | 20 | 700 | 1000 | 1.6 | 1.4 | 22 | 900 | 1200 | [17 empty] | 0.3
[28 empty] | 110700200035 | 35 | 6 | 6 | 1.2 | 0.8 | 1.4 | 22 | 800 | 1230 | 1.6 | 1.4 | 23 | 1030 | 1450 | [17 empty] | 0.3
[28 empty] | 110700200050 | 50 | 6 | 6 | 1.4 | 0.8 | 1.4 | 25 | 1000 | 1620 | 1.6 | 1.56 | 26 | 1300 | 1900 | [17 empty] | 0.4
[28 empty] | 110700200070 | 70 | 12 | 12 | 1.4 | 0.8 | 1.56 | 27 | 1200 | 2050 | 1.6 | 1.56 | 29 | 1500 | 2350 | [17 empty] | 0.4
[28 empty] | 110700200095 | 95 | 15 | 15 | 1.6 | 0.8 | 1.56 | 30 | 1550 | 2720 | 2 | 1.56 | 33 | 2050 | 3200 | [17 empty] | 0.4
[28 empty] | 110700200120 | 120 | 15 | 18 | 1.6 | 0.8 | 1.56 | 32 | 1800 | 3290 | 2 | 1.72 | 35 | 2400 | 3900 | [17 empty] | 0.5
[28 empty] | 110700200150 | 150 | 15 | 18 | 1.8 | 0.8 | 1.72 | 35 | 2100 | 3970 | 2 | 1.72 | 37 | 2760 | 4600 | [17 empty] | 0.5
[28 empty] | 110700200185 | 185 | 30 | 30 | 2 | 0.8 | 1.88 | 38 | 2500 | 4800 | 2 | 1.88 | 41 | 3200 | 5500 | [17 empty] | 0.6
[28 empty] | 110700200240 | 240 | 30 | 34 | 2.2 | 0.8 | 2.04 | 43 | 3100 | 6080 | 2.5 | 2.04 | 47 | 4200 | 7200 | [17 empty] | 0.6
[28 empty] | 110700200300 | 300 | 30 | 34 | 2.4 | 0.8 | 2.2 | 48 | 3700 | 7400 | 2.5 | 2.2 | 50 | 5000 | 8700 | [17 empty] | 0.7
[28 empty] | 110700200400 | 400 | 53 | 53 | 2.6 | 0.8 | 2.36 | 53 | 4500 | 9450 | 3.2 | 2.52 | 58 | 6600 | 11500 | [17 empty] | 0.7
[28 empty] | 110700200500 | 500 | 53 | 53 | 3 | 0.8 | 2.68 | 56 | 5600 | 11800 | 3.2 | 2.84 | 64 | 8000 | 14000 | [17 empty] | 0.7
[28 empty] | 110700200630 | 630 | 53 | 53 | 3.4 | 0.8 | 2.84 | 66 | 6900 | 14700 | 4 | 3 | 72 | 11000 | 18800 | [17 empty] | 0.7
[43 empty] | 110700200004 | 4 | _ | 4.61 | _ | 5.53 | 0.098 | 0.23 | 32 | 27 | 27 | 41 | 35 | 35 | 0.304 | 0.46
[43 empty] | 110700200006 | 6 | 4.61 | 3.08 | 5.53 | 3.7 | 0.096 | 0.28 | 40 | 34 | 35 | 50 | 44 | 45 | 0.456 | 0.69
[43 empty] | 110700200010 | 10 | 3.08 | 1.83 | 3.7 | 2.2 | 0.091 | 0.34 | 55 | 45 | 47 | 70 | 58 | 60 | 0.76 | 1.15
[43 empty] | 110700200016 | 16 | 1.91 | 1.15 | 2.29 | 1.38 | 0.085 | 0.4 | 70 | 58 | 59 | 90 | 75 | 78 | 1.22 | 1.84
[43 empty] | 110700200025 | 25 | 1.2 | 0.727 | 1.44 | 0.87 | 0.083 | 0.42 | 90 | 76 | 78 | 115 | 97 | 105 | 1.9 | 2.88
[43 empty] | 110700200035 | 35 | 0.868 | 0.524 | 1.04 | 0.63 | 0.082 | 0.48 | 110 | 92 | 99 | 140 | 120 | 125 | 2.66 | 4.03
[43 empty] | 110700200050 | 50 | 0.641 | 0.387 | 0.769 | 0.464 | 0.082 | 0.49 | 135 | 115 | 125 | 165 | 145 | 155 | 3.8 | 5.75
[43 empty] | 110700200070 | 70 | 0.443 | 0.268 | 0.532 | 0.322 | 0.076 | 0.56 | 160 | 140 | 150 | 205 | 180 | 195 | 5.32 | 8.05
[43 empty] | 110700200095 | 95 | 0.32 | 0.193 | 0.384 | 0.232 | 0.076 | 0.58 | 190 | 170 | 185 | 240 | 215 | 230 | 7.22 | 10.9
[43 empty] | 110700200120 | 120 | 0.253 | 0.153 | 0.304 | 0.184 | 0.075 | 0.63 | 210 | 190 | 210 | 275 | 235 | 265 | 9.12 | 13.8
[43 empty] | 110700200150 | 150 | 0.206 | 0.124 | 0.247 | 0.1488 | 0.074 | 0.63 | 240 | 210 | 240 | 310 | 270 | 305 | 11.4 | 17.3
[43 empty] | 110700200185 | 185 | 0.164 | 0.0991 | 0.197 | 0.1189 | 0.074 | 0.64 | 275 | 240 | 275 | 350 | 300 | 350 | 14.1 | 21.3
[43 empty] | 110700200240 | 240 | 0.125 | 0.0754 | 0.151 | 0.0912 | 0.073 | 0.67 | 320 | 275 | 325 | 405 | 345 | 410 | 18.2 | 27.6
[43 empty] | 110700200300 | 300 | 0.1 | 0.0601 | 0.122 | 0.0733 | 0.073 | 0.68 | 355 | 305 | 365 | 450 | 385 | 465 | 22.8 | 34.5
[43 empty] | 110700200400 | 400 | 0.0778 | 0.047 | 0.0961 | 0.058 | 0.072 | 0.7 | 385 | 345 | 420 | 490 | 485 | 530 | 30.4 | 46
[43 empty] | 110700200500 | 500 | 0.0605 | 0.0366 | 0.0759 | 0.0459 | 0.072 | 0.7 | 425 | 380 | 475 | 540 | 460 | 605 | 38 | 57.5
[43 empty] | 110700200630 | 630 | 0.0469 | 0.0283 | 0.061 | 0.0368 | 0.072 | 0.7 | 465 | 415 | 540 | 640 | 550 | 785 | 47.9 | 72.5
https://www.rrkabel.com/power-cables/power-cables-ayfyyfy-aywyywy-3-core | AYFY/YFY-AYWY/YWY-3 CORE | ['https://www.rrkabel.com/Uploads/Products/109/ProductZoomForMoreDetailsImage/02.png', 'https://www.rrkabel.com/Uploads/Products/109/ProductZoomImage/03-.jpg', 'https://www.rrkabel.com/Uploads/Products/325/ProductFeaturesDetails/01.png', 'https://www.rrkabel.com/Uploads/Products/325/ProductFeaturesDetails/01.png'] | ['1.1 kV (A.C) & 1.5 kV (D.C ) to Earth', '3 cores AL / CU conductor, PVC insulated, galvanised steel strip / wire armoured cables as per IS 1554 Part - 1.'] | ['AL up to 10 Sq. mm conductor are solid Cl. 1 as per IS 8130. And above 10 Sq. mm conductor are stranded compacted shape Cl. 2 as per IS 8130', 'In CU 4 & 6 Sq. mm conductor are solid Cl. 1 or stranded class-2 as per IS 8130. 10 Sq. mm conductor is stranded Cl. 2 round as per IS 8130. Above 10 Sq. mm conductor are stranded compacted shaped Cl. 2 as per IS 8130'] | ['PVC Type - A as per IS 5831. (Option : PVC Type - C as per IS 5831)'] | ['Red, yellow, blue'] | ['PVC Type ST-1 as per IS 5831 (Option : PVC Type ST - 2 as per IS 5831, FR Type, FRLS Type)'] | [9 empty] | ['PVC / PVC tape as per IS 1554 (P - 1)'] | [8 empty] | ['Single armouring of galvanised steel strip / wire']
[28 empty] | 110800300004 | 4 | _ | 1/7 | 1 | [5 empty] | 1.4 | 1.24 | 18 | 570 | 620 | [17 empty] | 0.3
[28 empty] | 110800300006 | 6 | 1 | 1/7 | 1 | [5 empty] | 1.4 | 1.24 | 19 | 670 | 780 | [17 empty] | 0.3
[28 empty] | 110800300010 | 10 | 1 | 6 | 1 | [5 empty] | 1.4 | 1.4 | 21 | 870 | 1080 | [17 empty] | 0.3
[28 empty] | 110800300016 | 16 | 6 | 6 | 1 | 0.8 | 1.4 | 20 | 690 | 990 | 1.6 | 1.4 | 21 | 920 | 1230 | [17 empty] | 0.3
[28 empty] | 110800300025 | 25 | 6 | 6 | 1.2 | 0.8 | 1.4 | 23 | 890 | 1340 | 1.6 | 1.4 | 23 | 1070 | 1520 | [17 empty] | 0.3
[28 empty] | 110800300035 | 35 | 6 | 6 | 1.2 | 0.8 | 1.4 | 24 | 990 | 1640 | 1.6 | 1.56 | 26 | 1280 | 1930 | [17 empty] | 0.3
[28 empty] | 110800300050 | 50 | 6 | 6 | 1.4 | 0.8 | 1.56 | 27 | 1300 | 2220 | 1.6 | 1.56 | 29 | 1580 | 2510 | [17 empty] | 0.4
[28 empty] | 110800300070 | 70 | 12 | 12 | 1.4 | 0.8 | 1.56 | 31 | 1590 | 2900 | 2 | 1.56 | 33 | 2130 | 3430 | [17 empty] | 0.4
[28 empty] | 110800300095 | 95 | 15 | 15 | 1.6 | 0.8 | 1.56 | 35 | 1990 | 3740 | 2 | 1.72 | 37 | 2630 | 4380 | [17 empty] | 0.4
[28 empty] | 110800300120 | 120 | 15 | 18 | 1.6 | 0.8 | 1.72 | 37 | 2390 | 4620 | 2 | 1.88 | 39 | 2980 | 5180 | [17 empty] | 0.5
[28 empty] | 110800300150 | 150 | 15 | 18 | 1.8 | 0.8 | 1.88 | 41 | 2790 | 5600 | 2 | 2.04 | 43 | 3530 | 6280 | [17 empty] | 0.5
[28 empty] | 110800300185 | 185 | 30 | 30 | 2 | 0.8 | 1.88 | 46 | 3400 | 6830 | 2.5 | 2.2 | 49 | 4590 | 7980 | [17 empty] | 0.6
[28 empty] | 110800300240 | 240 | 30 | 34 | 2.2 | 0.8 | 2.2 | 51 | 4200 | 8640 | 2.5 | 2.36 | 54 | 5580 | 9980 | [17 empty] | 0.6
[28 empty] | 110800300300 | 300 | 30 | 34 | 2.4 | 0.8 | 2.36 | 56 | 5040 | 10620 | 2.5 | 2.68 | 59 | 6580 | 11980 | [17 empty] | 0.7
[28 empty] | 110800300400 | 400 | 53 | 53 | 2.6 | 0.8 | 2.68 | 63 | 6290 | 13730 | 3.2 | 2.84 | 68 | 8690 | 15990 | [17 empty] | 0.7
[28 empty] | 110800300500 | 500 | 53 | 53 | 3 | 0.8 | 3 | 70 | 7790 | 17090 | 3.2 | 3 | 75 | 10980 | 19980 | [17 empty] | 0.7
[28 empty] | 110800300630 | 630 | 53 | 53 | 3.4 | 0.8 | 3 | 78 | 9690 | 21410 | 4 | 3 | 84 | 15990 | 25480 | [17 empty] | 0.7
[43 empty] | 110800300004 | 4 | _ | 4.61 | _ | 5.53 | 0.098 | 0.23 | 28 | 23 | 23 | 36 | 30 | 30 | 0.304 | 0.46
[43 empty] | 110800300006 | 6 | 4.61 | 3.08 | 5.53 | 3.7 | 0.096 | 0.28 | 35 | 30 | 30 | 45 | 38 | 39 | 0.456 | 0.69
[43 empty] | 110800300010 | 10 | 3.08 | 1.83 | 3.7 | 2.2 | 0.091 | 0.34 | 46 | 39 | 40 | 60 | 50 | 52 | 0.76 | 1.15
[43 empty] | 110800300016 | 16 | 1.91 | 1.15 | 2.29 | 1.38 | 0.085 | 0.4 | 60 | 50 | 51 | 77 | 64 | 66 | 1.22 | 1.84
[43 empty] | 110800300025 | 25 | 1.2 | 0.727 | 1.44 | 0.87 | 0.083 | 0.42 | 76 | 63 | 70 | 99 | 81 | 90 | 1.9 | 2.88
[43 empty] | 110800300035 | 35 | 0.868 | 0.524 | 1.04 | 0.63 | 0.082 | 0.48 | 92 | 77 | 86 | 120 | 99 | 110 | 2.66 | 4.03
[43 empty] | 110800300050 | 50 | 0.641 | 0.387 | 0.769 | 0.464 | 0.082 | 0.49 | 110 | 95 | 105 | 145 | 125 | 135 | 3.8 | 5.75
[43 empty] | 110800300070 | 70 | 0.443 | 0.268 | 0.532 | 0.322 | 0.076 | 0.56 | 135 | 115 | 130 | 175 | 150 | 165 | 5.32 | 8.05
[43 empty] | 110800300095 | 95 | 0.32 | 0.193 | 0.384 | 0.232 | 0.076 | 0.58 | 165 | 140 | 155 | 210 | 175 | 200 | 7.22 | 10.9
[43 empty] | 110800300120 | 120 | 0.253 | 0.153 | 0.304 | 0.184 | 0.075 | 0.63 | 185 | 155 | 180 | 240 | 195 | 230 | 9.12 | 13.8
[43 empty] | 110800300150 | 150 | 0.206 | 0.124 | 0.247 | 0.1488 | 0.074 | 0.63 | 210 | 175 | 205 | 270 | 225 | 265 | 11.4 | 17.3
[43 empty] | 110800300185 | 185 | 0.164 | 0.0991 | 0.197 | 0.1189 | 0.074 | 0.64 | 235 | 200 | 240 | 300 | 255 | 305 | 14.1 | 21.3
[43 empty] | 110800300240 | 240 | 0.125 | 0.0754 | 0.151 | 0.0912 | 0.073 | 0.67 | 275 | 235 | 280 | 345 | 295 | 355 | 18.2 | 27.6
[43 empty] | 110800300300 | 300 | 0.1 | 0.0601 | 0.122 | 0.0733 | 0.073 | 0.68 | 305 | 260 | 315 | 385 | 335 | 400 | 22.8 | 34.5
[43 empty] | 110800300400 | 400 | 0.0778 | 0.047 | 0.0961 | 0.058 | 0.072 | 0.7 | 335 | 290 | 375 | 425 | 360 | 435 | 30.4 | 46
[43 empty] | 110800300500 | 500 | 0.0605 | 0.0366 | 0.0759 | 0.0459 | 0.072 | 0.7 | 370 | 320 | 425 | 470 | 390 | 520 | 38 | 57.5
[43 empty] | 110800300630 | 630 | 0.0469 | 0.0283 | 0.061 | 0.0368 | 0.072 | 0.7 | 405 | 350 | 480 | 555 | 470 | 675 | 47.9 | 72.5
https://www.rrkabel.com/power-cables/power-cables-ayfyyfy-aywyywy-3-5-core | AYFY/YFY-AYWY/YWY-3.5 CORE | ['https://www.rrkabel.com/Uploads/Products/110/ProductZoomForMoreDetailsImage/02-.jpg', 'https://www.rrkabel.com/Uploads/Products/110/ProductZoomImage/03-.jpg', 'https://www.rrkabel.com/Uploads/Products/328/ProductFeaturesDetails/01.png', 'https://www.rrkabel.com/Uploads/Products/328/ProductFeaturesDetails/01.png'] | ['1.1 kV (A.C) & 1.5 kV (D.C ) to Earth', '3.5 cores AL /CU Conductor, PVC insulated, galvanised steel strip /wire armoured cables as per IS 1554 Part -1.'] | ['AL/ CU Stranded compact shaped conductor as per Cl. 2, IS 8130'] | ['PVC Type - A as per IS 5831. (Option : HR PVC Type - C, as per IS 5831)'] |  | ['PVC Type ST - 1 as per IS 5831 (Option : PVC Type ST - 2 as per IS 5831, FR Type, FRLS Type)'] | [9 empty] | ['PVC / PVC tape as per IS 1554 (P - 1)'] | [8 empty] | ['Single armouring of galvanised steel strip / wire'] | [34 empty] | ['Red, yellow, blue'] | ['Black']
[28 empty] | 110901010211 | 3×25+16 | 6/6 | 6/6 | 1.2/1.0 | 0.8 | 1.4 | 24 | 1000 | 1550 | 1.6 | 1.4 | 26 | 1285 | 1825 | [17 empty] | 0.3
[28 empty] | 110901020211 | 3×35+16 | 6/6 | 6/6 | 1.2/1.0 | 0.8 | 1.4 | 26 | 1200 | 1950 | 1.6 | 1.4 | 28 | 1425 | 2125 | [17 empty] | 0.3
[28 empty] | 110901030211 | 3×50+25 | 6/6 | 6/6 | 1.4/1.2 | 0.8 | 1.56 | 30 | 1500 | 2600 | 1.6 | 1.56 | 31 | 1785 | 2790 | [17 empty] | 0.3
[28 empty] | 110901040211 | 3×70+35 | 12/6 | 12/6 | 1.4/1.2 | 0.8 | 1.56 | 34 | 1800 | 3300 | 2 | 1.56 | 36 | 2390 | 3780 | [17 empty] | 0.4
[28 empty] | 110901050211 | 3×95+50 | 15/6 | 15/6 | 1.6/1.4 | 0.8 | 1.56 | 37 | 2300 | 4350 | 2 | 1.72 | 39 | 2980 | 4980 | [17 empty] | 0.4
[28 empty] | 110901060211 | 3×120+70 | 15/12 | 18/12 | 1.6/1.4 | 0.8 | 1.72 | 41 | 2800 | 5450 | 2 | 1.88 | 43 | 3480 | 6080 | [17 empty] | 0.5
[28 empty] | 110901070211 | 3×150+70 | 15/12 | 18/12 | 1.8/1.4 | 0.8 | 1.88 | 45 | 3200 | 6400 | 2 | 1.88 | 47 | 3970 | 7180 | [17 empty] | 0.5
[28 empty] | 110901080211 | 3×185+95 | 30/15 | 30/15 | 2/1.6 | 0.8 | 2.04 | 49 | 3900 | 7900 | 2.5 | 2.04 | 53 | 5185 | 9150 | [17 empty] | 0.5
[28 empty] | 110901090211 | 3×240+120 | 30/15 | 34/18 | 2.20/1.6 | 0.8 | 2.2 | 55 | 4800 | 10000 | 2.5 | 2.3 | 58 | 6385 | 11480 | [17 empty] | 0.6
[28 empty] | 110901100211 | 3×300+150 | 30/15 | 34/18 | 2.4/1.8 | 0.8 | 2.36 | 61 | 5800 | 12300 | 3.2 | 2.52 | 65 | 8180 | 14480 | [17 empty] | 0.6
[28 empty] | 110901110211 | 3×400+185 | 53/30 | 53/30 | 2.6/2.0 | 0.8 | 2.68 | 69 | 7300 | 15800 | 3.2 | 2.63 | 75 | 9885 | 18380 | [17 empty] | 0.7
[28 empty] | 110901120211 | 3×500+240 | 53/30 | 53/34 | 3.0/2.2 | 0.8 | 2.84 | 77 | 9000 | 19500 | 4 | 3 | 84 | 13480 | 23985 | [17 empty] | 0.7
[28 empty] | 110901130211 | 3×630+300 | 53/30 | 53/34 | 3.4/2.40 | 0.8 | 3 | 87 | 11500 | 25000 | 4 | 3 | 92 | 15980 | 28480 | [17 empty] | 0.7
[43 empty] | 110901010211 | 3×25+16 | 1.2 | 0.727 | 1.44 | 0.87 | 0.083 | 0.42 | 76 | 63 | 70 | 99 | 81 | 90 | 1.9 | 2.88
[43 empty] | 110901020211 | 3×35+16 | 0.868 | 0.524 | 1.04 | 0.63 | 0.082 | 0.48 | 92 | 77 | 86 | 120 | 99 | 110 | 2.66 | 4.03
[43 empty] | 110901030211 | 3×50+25 | 0.641 | 0.387 | 0.769 | 0.464 | 0.082 | 0.49 | 110 | 95 | 105 | 145 | 125 | 135 | 3.8 | 5.75
[43 empty] | 110901040211 | 3×70+35 | 0.443 | 0.268 | 0.532 | 0.322 | 0.076 | 0.56 | 135 | 115 | 130 | 175 | 150 | 165 | 5.32 | 8.05
[43 empty] | 110901050211 | 3×95+50 | 0.32 | 0.193 | 0.384 | 0.232 | 0.076 | 0.58 | 165 | 140 | 155 | 210 | 175 | 200 | 7.22 | 10.9
[43 empty] | 110901060211 | 3×120+70 | 0.253 | 0.153 | 0.304 | 0.184 | 0.075 | 0.63 | 185 | 155 | 180 | 240 | 195 | 230 | 9.12 | 13.8
[43 empty] | 110901070211 | 3×150+70 | 0.206 | 0.124 | 0.247 | 0.1488 | 0.074 | 0.63 | 210 | 175 | 205 | 270 | 225 | 265 | 11.4 | 17.3
[43 empty] | 110901080211 | 3×185+95 | 0.164 | 0.0991 | 0.197 | 0.1189 | 0.074 | 0.64 | 235 | 200 | 240 | 300 | 255 | 305 | 14.1 | 21.3
[43 empty] | 110901090211 | 3×240+120 | 0.125 | 0.0754 | 0.151 | 0.0912 | 0.073 | 0.67 | 275 | 235 | 280 | 345 | 295 | 355 | 18.2 | 27.6
[43 empty] | 110901100211 | 3×300+150 | 0.1 | 0.0601 | 0.122 | 0.0733 | 0.073 | 0.68 | 305 | 260 | 315 | 385 | 335 | 400 | 22.8 | 34.5
[43 empty] | 110901110211 | 3×400+185 | 0.0778 | 0.047 | 0.0961 | 0.058 | 0.072 | 0.7 | 335 | 290 | 375 | 425 | 360 | 435 | 30.4 | 46
[43 empty] | 110901120211 | 3×500+240 | 0.0605 | 0.0366 | 0.0759 | 0.459 | 0.072 | 0.7 | 370 | 320 | 425 | 470 | 390 | 520 | 38 | 57.5
[43 empty] | 110901130211 | 3×630+300 | 0.0469 | 0.0283 | 0.061 | 0.0368 | 0.072 | 0.7 | 405 | 350 | 480 | 555 | 470 | 675 | 47.9 | 72.5
https://www.rrkabel.com/power-cables/power-cables-ayfyyfy-aywyywy-4-core | AYFY/YFY-AYWY/YWY-4 CORE | ['https://www.rrkabel.com/Uploads/Products/111/ProductZoomForMoreDetailsImage/02-.jpg', 'https://www.rrkabel.com/Uploads/Products/111/ProductZoomImage/03-.jpg', 'https://www.rrkabel.com/Uploads/Products/331/ProductFeaturesDetails/01.png', 'https://www.rrkabel.com/Uploads/Products/331/ProductFeaturesDetails/01.png'] | ['1.1 kV (A.C) & 1.5 kV (D.C ) to Earth', '4 Cores AL / CU conductor, PVC insulated, galvanised steel strip / wire armoured cables as per IS 1554 Part - 1.'] | ['AL up to 10 Sq. mm conductor are solid Cl. 1 as per IS 8130. And above 10 Sq. mm conductor are stranded compacted shape Cl. 2 as per IS 8130', 'In CU 4 & 6 Sq. mm conductor are solid Cl. 1 or stranded Cl. 2 as per IS 8130. 10 Sq. mm conductor is stranded Cl. 2 round as per IS 8130. Above 10 Sq. mm conductor are stranded compacted shaped Cl.2 as per IS 8130'] | ['PVC Type - A as per IS 5831. (Option : PVC Type - C as per IS 5831)'] | ['Red, yellow, blue, black'] | ['PVC Type ST - 1 as per IS 5831 (Option : PVC Type ST - 2 as per IS 5831, FR Type, FRLS Type)'] | [9 empty] | ['PVC / PVC tape as per IS 1554 (P-1)'] | [8 empty] | ['Single armouring of galvanised steel strip / wire'] | [32 empty] | ['While ordering, in addition to the part number the following details shall also be advised: Conductor Type (Aluminium or Copper) and class of conductor (Cl. 1 or 2). Insulation Type – PVC Type A / C. Sheath Type – PVC Type ST-1 / FR / FRLS; PVC Type ST-2 / FR / FRLS.']
[28 empty] | 111000400004 | 4 | _ | 1/7 | 1 | [5 empty] | 1.4 | 1.24 | 18 | 630 | 775 | [17 empty] | 0.3
[28 empty] | 111000400006 | 6 | 1 | 1/7 | 1 | [5 empty] | 1.4 | 1.24 | 21 | 870 | 1010 | [17 empty] | 0.3
[28 empty] | 111000400010 | 10 | 1 | 6 | 1 | 0.8 | 1.4 | 21 | 750 | 998 | 1.6 | 1.4 | 22 | 890 | 1130 | [17 empty] | 0.3
[28 empty] | 111000400016 | 16 | 6 | 6 | 1 | 0.8 | 1.4 | 22 | 860 | 1260 | 1.6 | 1.4 | 23 | 1110 | 1500 | [17 empty] | 0.3
[28 empty] | 111000400025 | 25 | 6 | 6 | 1.2 | 0.8 | 1.4 | 25 | 1100 | 1720 | 1.6 | 1.4 | 27 | 1385 | 2000 | [17 empty] | 0.3
[28 empty] | 111000400035 | 35 | 6 | 6 | 1.2 | 0.8 | 1.4 | 28 | 1300 | 2170 | 1.6 | 1.56 | 30 | 1580 | 2450 | [17 empty] | 0.3
[28 empty] | 111000400050 | 50 | 6 | 6 | 1.4 | 0.8 | 1.56 | 32 | 1600 | 2850 | 2 | 1.56 | 34 | 2185 | 3425 | [17 empty] | 0.4
[28 empty] | 111000400070 | 70 | 12 | 12 | 1.4 | 0.8 | 1.56 | 35 | 2000 | 3740 | 2 | 1.56 | 37 | 2625 | 4370 | [17 empty] | 0.4
[28 empty] | 111000400095 | 95 | 15 | 15 | 1.6 | 0.8 | 1.72 | 40 | 2600 | 5000 | 2 | 1.72 | 42 | 3285 | 5640 | [17 empty] | 0.4
[28 empty] | 111000400120 | 120 | 15 | 18 | 1.6 | 0.8 | 1.88 | 43 | 3050 | 6030 | 2 | 1.88 | 47 | 3825 | 6820 | [17 empty] | 0.5
[28 empty] | 111000400150 | 150 | 15 | 18 | 1.8 | 0.8 | 1.88 | 48 | 3600 | 7325 | 2.5 | 2.04 | 51 | 4830 | 8560 | [17 empty] | 0.5
[28 empty] | 111000400185 | 185 | 30 | 30 | 2 | 0.8 | 2.04 | 52 | 4300 | 8890 | 2.5 | 2.2 | 56 | 5780 | 10370 | [17 empty] | 0.6
[28 empty] | 111000400240 | 240 | 30 | 34 | 2.2 | 0.8 | 2.36 | 59 | 5400 | 11355 | 2.5 | 2.36 | 62 | 7685 | 12940 | [17 empty] | 0.6
[28 empty] | 111000400300 | 300 | 30 | 34 | 2.4 | 0.8 | 2.52 | 67 | 6600 | 14050 | 3.2 | 2.68 | 70 | 9185 | 16630 | [17 empty] | 0.7
[28 empty] | 111000400400 | 400 | 53 | 53 | 2.6 | 0.8 | 2.84 | 74 | 8200 | 18128 | 3.2 | 2.84 | 76 | 10980 | 20390 | [17 empty] | 0.7
[28 empty] | 111000400500 | 500 | 53 | 53 | 3 | 0.8 | 3 | 80 | 10500 | 22900 | 4 | 3 | 86 | 14980 | 27360 | [17 empty] | 0.7
[28 empty] | 111000400630 | 630 | 53 | 53 | 3.4 | 0.8 | 3 | 90 | 13000 | 28625 | 4 | 3 | 96 | 17975 | 33600 | [17 empty] | 0.7
[43 empty] | 111000400004 | 4 | _ | 4.61 | _ | 5.53 | 0.098 | 0.23 | 28 | 23 | 23 | 36 | 30 | 30 | 0.304 | 0.46
[43 empty] | 111000400006 | 6 | 4.61 | 3.08 | 5.53 | 3.7 | 0.096 | 0.28 | 35 | 30 | 30 | 45 | 38 | 39 | 0.456 | 0.69
[43 empty] | 111000400010 | 10 | 3.08 | 1.83 | 3.7 | 2.2 | 0.091 | 0.34 | 46 | 39 | 40 | 60 | 50 | 52 | 0.76 | 1.15
[43 empty] | 111000400016 | 16 | 1.91 | 1.15 | 2.29 | 1.38 | 0.085 | 0.4 | 60 | 50 | 51 | 77 | 64 | 66 | 1.22 | 1.84
[43 empty] | 111000400025 | 25 | 1.2 | 0.727 | 1.44 | 0.87 | 0.083 | 0.42 | 76 | 63 | 70 | 99 | 81 | 90 | 1.9 | 2.88
[43 empty] | 111000400035 | 35 | 0.868 | 0.524 | 1.04 | 0.63 | 0.082 | 0.48 | 92 | 77 | 86 | 120 | 99 | 110 | 2.66 | 4.03
[43 empty] | 111000400050 | 50 | 0.641 | 0.387 | 0.769 | 0.464 | 0.082 | 0.49 | 110 | 95 | 105 | 145 | 125 | 135 | 3.8 | 5.75
[43 empty] | 111000400070 | 70 | 0.443 | 0.268 | 0.532 | 0.322 | 0.076 | 0.56 | 135 | 115 | 130 | 175 | 150 | 165 | 5.32 | 8.05
[43 empty] | 111000400095 | 95 | 0.32 | 0.193 | 0.384 | 0.232 | 0.076 | 0.58 | 165 | 140 | 155 | 210 | 175 | 200 | 7.22 | 10.9
[43 empty] | 111000400120 | 120 | 0.253 | 0.153 | 0.304 | 0.184 | 0.075 | 0.63 | 185 | 155 | 180 | 240 | 195 | 230 | 9.12 | 13.8
[43 empty] | 111000400150 | 150 | 0.206 | 0.124 | 0.247 | 0.1488 | 0.074 | 0.63 | 210 | 175 | 205 | 270 | 225 | 265 | 11.4 | 17.3
[43 empty] | 111000400185 | 185 | 0.164 | 0.0991 | 0.197 | 0.1189 | 0.074 | 0.64 | 235 | 200 | 240 | 300 | 255 | 305 | 14.1 | 21.3
[43 empty] | 111000400240 | 240 | 0.125 | 0.0754 | 0.151 | 0.0912 | 0.073 | 0.67 | 275 | 235 | 280 | 345 | 295 | 355 | 18.2 | 27.6
[43 empty] | 111000400300 | 300 | 0.1 | 0.0601 | 0.122 | 0.0733 | 0.073 | 0.68 | 305 | 260 | 315 | 385 | 335 | 400 | 22.8 | 34.5
[43 empty] | 111000400400 | 400 | 0.0778 | 0.047 | 0.0961 | 0.058 | 0.072 | 0.7 | 335 | 290 | 375 | 425 | 360 | 435 | 30.4 | 46
[43 empty] | 111000400500 | 500 | 0.0605 | 0.0366 | 0.0759 | 0.0459 | 0.072 | 0.7 | 370 | 320 | 425 | 470 | 390 | 520 | 38 | 57.5
[43 empty] | 111000400630 | 630 | 0.0469 | 0.0283 | 0.061 | 0.0368 | 0.072 | 0.7 | 405 | 350 | 480 | 555 | 470 | 675 | 47.9 | 72.5
https://www.rrkabel.com/power-cables/power-cables-yyyfyywy-1-5-sq-mm | YY/YFY/YWY-1.5 Sq. mm | ['https://www.rrkabel.com/Uploads/Products/112/ProductZoomForMoreDetailsImage/02-.jpg', 'https://www.rrkabel.com/Uploads/Products/112/ProductZoomImage/03-.jpg', 'https://www.rrkabel.com/Uploads/Products/334/ProductFeaturesDetails/01.png', 'https://www.rrkabel.com/Uploads/Products/334/ProductFeaturesDetails/01.png'] | ['1.1 kV (A.C) & 1.5 kV (D.C ) to Earth', '1.5 Sq. mm copper conductor, PVC insulated unarmoured & galvanised steel strip / wire armoured control cables as per IS 1554 Part - 1.'] | ['CU conductor solid as per Cl.1 IS 8130 or stranded as per Cl. 2 IS 8130'] |  |  | ['PVC Type ST - 1 as per IS 5831 (Option : PVC Type ST - 2 as per IS 5831, FR Type / FRLS Type)'] | [9 empty] | ['PVC / PVC tape as per IS 1554 (P - 1)'] | [8 empty] | ['Single armouring of galvanised steel strip / wire'] | [32 empty] | ['While ordering, in addition to the part number the following details shall also be advised: Conductor Type (Aluminium or Copper) and class of conductor (Cl. 1 or 2). Insulation Type – PVC Type A / C. Sheath Type – PVC Type ST-1 / FR / FRLS; PVC Type ST-2 / FR / FRLS.'] |  |  |  | ['PVC Type - A as per IS 5831 / Option : HR PVC (Type - C ) as per IS 5831. Nominal Thickness of Insulation is 0.8 mm.'] | ['Up to 5 cores by colour coding & more than 5 cores number printing on core as per IS 1554 (P-1)']
[8 empty] | 111100201105 | [9 empty] | 0.3 | [46 empty] | 2 | 1.8 | 12 | 180 |  |  |  |  | 1.4 | 1.24 | 13 | 380
[8 empty] | 111100301105 | [9 empty] | 0.3 | [46 empty] | 3 | 1.8 | 12.5 | 200 |  |  |  |  | 1.4 | 1.24 | 14 | 440
[8 empty] | 111100401105 | [9 empty] | 0.3 | [46 empty] | 4 | 1.8 | 13 | 230 |  |  |  |  | 1.4 | 1.24 | 15 | 480
[8 empty] | 111100501105 | [9 empty] | 0.3 | [46 empty] | 5 | 1.8 | 14 | 250 |  |  |  |  | 1.4 | 1.24 | 16 | 510
[8 empty] | 111100601105 | [9 empty] | 0.3 | [46 empty] | 6 | 1.8 | 15 | 290 |  |  |  |  | 1.4 | 1.24 | 17 | 570
[8 empty] | 111100701105 | [9 empty] | 0.3 | [46 empty] | 7 | 1.8 | 15 | 310 |  |  |  |  | 1.4 | 1.24 | 17 | 630
[8 empty] | 111101001105 | [9 empty] | 0.3 | [46 empty] | 10 | 1.8 | 18 | 420 |  |  |  |  | 1.4 | 1.24 | 20 | 780
[8 empty] | 111101201105 | [9 empty] | 0.3 | [46 empty] | 12 | 1.8 | 19 | 470 | 0.8 | 1.24 | 19 | 700 | 1.6 | 1.4 | 21 | 900
[8 empty] | 111101401105 | [9 empty] | 0.3 | [46 empty] | 14 | 1.8 | 20 | 530 | 0.8 | 1.4 | 20 | 800 | 1.6 | 1.4 | 22 | 980
[8 empty] | 111101601105 | [9 empty] | 0.3 | [46 empty] | 16 | 1.8 | 21 | 600 | 0.8 | 1.4 | 21 | 850 | 1.6 | 1.4 | 23 | 1050
[8 empty] | 111101901105 | [9 empty] | 0.3 | [46 empty] | 19 | 2 | 22 | 700 | 0.8 | 1.4 | 22 | 950 | 1.6 | 1.4 | 24 | 1160
[8 empty] | 111102401105 | [9 empty] | 0.3 | [46 empty] | 24 | 2 | 25 | 850 | 0.8 | 1.4 | 25 | 1150 | 1.6 | 1.4 | 27 | 1400
[8 empty] | 111102701105 | [9 empty] | 0.3 | [46 empty] | 27 | 2 | 26 | 920 | 0.8 | 1.4 | 26 | 1250 | 1.6 | 1.4 | 28 | 1480
[8 empty] | 111103001105 | [9 empty] | 0.3 | [46 empty] | 30 | 2 | 27 | 1000 | 0.8 | 1.4 | 27 | 1330 | 1.6 | 1.4 | 29 | 1600
[8 empty] | 111103701105 | [9 empty] | 0.3 | [46 empty] | 37 | 2 | 28 | 1200 | 0.8 | 1.4 | 29 | 1530 | 1.6 | 1.4 | 30 | 1800
[8 empty] | 111104001105 | [9 empty] | 0.3 | [46 empty] | 40 | 2 | 29 | 1270 | 0.8 | 1.4 | 30 | 1650 | 1.6 | 1.56 | 32 | 1980
[8 empty] | 111104401105 | [9 empty] | 0.3 | [46 empty] | 44 | 2 | 31 | 1400 | 0.8 | 1.56 | 32 | 1850 | 1.6 | 1.56 | 34 | 2150
[8 empty] | 111105201105 | [9 empty] | 0.4 | [46 empty] | 52 | 2 | 33 | 1650 | 0.8 | 1.56 | 34 | 2050 | 2 | 1.56 | 36 | 2650
[8 empty] | 111106101105 | [9 empty] | 0.4 | [46 empty] | 61 | 2.2 | 35 | 1850 | 0.8 | 1.56 | 35 | 2300 | 2 | 1.56 | 38 | 2950
https://www.rrkabel.com/power-cables/power-cables-yyyfyywy-2-5-sq-mm | YY/YFY/YWY-2.5 Sq. mm | ['https://www.rrkabel.com/Uploads/Products/113/ProductZoomForMoreDetailsImage/02-.jpg', 'https://www.rrkabel.com/Uploads/Products/113/ProductZoomImage/03-.jpg', 'https://www.rrkabel.com/Uploads/Products/337/ProductFeaturesDetails/01.png', 'https://www.rrkabel.com/Uploads/Products/337/ProductFeaturesDetails/01.png'] | ['1.1 kV (A.C) & 1.5 kV (D.C ) to Earth', '2.5 Sq. mm copper conductor, PVC insulated unarmoured & galvanised steel strip / wire armoured control cables as per IS 1554 Part - 1.'] | ['CU conductor solid as per Cl .1 IS 8130 or stranded as per Cl. 2 IS 8130'] |  |  | ['PVC Type ST - 1 as per IS 5831 (Option : PVC Type ST - 2 as per IS 5831, FR Type / FRLS Type)'] | [9 empty] | ['PVC / PVC tape as per IS 1554 (P - 1)'] | [8 empty] | ['Single armouring of galvanised steel strip / wire'] | [32 empty] | ['While ordering, in addition to the part number the following details shall also be advised: Class of conductor – Cl. 1 or 2. Insulation Type – PVC Type A / C. Sheath Type – PVC Type ST – 1 / FR / FRLS; PVC Type ST – 2 / FR / FRLS.'] |  |  |  | ['PVC Type - A as per IS 5831/ Option : HR PVC (Type - C) as per IS 5831. Nominal thickness of insulation is 0.9 mm'] | ['Up to 5 cores by colour coding & more than 5 cores number printing on core as per IS 1554 (P - 1)']
[8 empty] | 111200201205 | [9 empty] | 0.3 | [46 empty] | 2 | 1.8 | 13 | 220 |  |  |  |  | 1.4 | 1.24 | 14 | 440
[8 empty] | 111200301205 | [9 empty] | 0.3 | [46 empty] | 3 | 1.8 | 14 | 260 |  |  |  |  | 1.4 | 1.24 | 15 | 480
[8 empty] | 111200401205 | [9 empty] | 0.3 | [46 empty] | 4 | 1.8 | 15 | 310 |  |  |  |  | 1.4 | 1.24 | 16 | 560
[8 empty] | 111200501205 | [9 empty] | 0.3 | [46 empty] | 5 | 1.8 | 16 | 340 |  |  |  |  | 1.4 | 1.24 | 17 | 600
[8 empty] | 111200601205 | [9 empty] | 0.3 | [46 empty] | 6 | 1.8 | 17 | 390 |  |  |  |  | 1.4 | 1.24 | 19 | 685
[8 empty] | 111200701205 | [9 empty] | 0.3 | [46 empty] | 7 | 1.8 | 17 | 424 |  |  |  |  | 1.6 | 1.24 | 19 | 720
[8 empty] | 111201001205 | [9 empty] | 0.3 | [46 empty] | 10 | 1.8 | 20 | 570 | 0.8 | 1.4 | 21 | 850 | 1.6 | 1.4 | 23 | 1040
[8 empty] | 111201201205 | [9 empty] | 0.3 | [46 empty] | 12 | 2 | 21 | 670 | 0.8 | 1.4 | 22 | 950 | 1.6 | 1.4 | 24 | 1130
[8 empty] | 111201401205 | [9 empty] | 0.3 | [46 empty] | 14 | 2 | 22 | 750 | 0.8 | 1.4 | 23 | 1050 | 1.6 | 1.4 | 25 | 1080
[8 empty] | 111201601205 | [9 empty] | 0.3 | [46 empty] | 16 | 2 | 24 | 840 | 0.8 | 1.4 | 24 | 1120 | 1.6 | 1.4 | 26 | 1180
[8 empty] | 111201901205 | [9 empty] | 0.3 | [46 empty] | 19 | 2 | 25 | 950 | 0.8 | 1.4 | 25 | 1250 | 1.6 | 1.4 | 27 | 1340
[8 empty] | 111202401205 | [9 empty] | 0.3 | [46 empty] | 24 | 2 | 28 | 1200 | 0.8 | 1.4 | 29 | 1550 | 1.6 | 1.56 | 31 | 1680
[8 empty] | 111202701205 | [9 empty] | 0.3 | [46 empty] | 27 | 2 | 29 | 1300 | 0.8 | 1.4 | 30 | 1650 | 1.6 | 1.56 | 32 | 1840
[8 empty] | 111203001205 | [9 empty] | 0.3 | [46 empty] | 30 | 2 | 30 | 1400 | 0.8 | 1.56 | 31 | 1800 | 1.6 | 1.56 | 33 | 1985
[8 empty] | 111203701205 | [9 empty] | 0.4 | [46 empty] | 37 | 2.2 | 33 | 1700 | 0.8 | 1.56 | 34 | 2100 | 2 | 1.56 | 36 | 2580
[8 empty] | 111204001205 | [9 empty] | 0.4 | [46 empty] | 40 | 2.2 | 34 | 1850 | 0.8 | 1.56 | 35 | 2300 | 2 | 1.56 | 37 | 2740
[8 empty] | 111204401205 | [9 empty] | 0.4 | [46 empty] | 44 | 2.2 | 36 | 2000 | 0.8 | 1.56 | 37 | 2500 | 2 | 1.56 | 40 | 2980
[8 empty] | 111205201205 | [9 empty] | 0.4 | [46 empty] | 52 | 2.2 | 38 | 2350 | 0.8 | 1.56 | 39 | 2850 | 2 | 1.72 | 42 | 3380
[8 empty] | 111206101205 | [9 empty] | 0.4 | [46 empty] | 61 | 2.2 | 40 | 2700 | 0.8 | 1.56 | 41 | 3250 | 2 | 1.72 | 44 | 3780
https://www.rrkabel.com/power-cables/power-cables-a2xy2xy-1-core | A2XY/2XY-1 CORE | ['https://www.rrkabel.com/Uploads/Products/114/ProductZoomForMoreDetailsImage/copper-A2XY-2XY-1-Core.jpg', 'https://www.rrkabel.com/Uploads/Products/114/ProductZoomImage/03-.jpg', 'https://www.rrkabel.com/Uploads/Products/340/ProductFeaturesDetails/01.png', 'https://www.rrkabel.com/Uploads/Products/340/ProductFeaturesDetails/01.png'] | ['1.1 kV (A.C) & 1.5 kV (D.C ) to Earth', '1 cores AL / CU conductor, XLPE insulated, unarmoured cables as per IS 7098 Part - 1.'] | ['AL up to 10 Sq. mm conductor are solid Cl. 1 as per IS 8130. And above 10 Sq. mm conductor are stranded round or compact Cl. 2 as per IS 8130', 'In CU 4 & 6 Sq. mm conductor are solid Cl. 1 or stranded Cl. 2 as per IS 8130. 10 Sq. mm & above stranded round or stranded compact Cl. 2 as per IS 8130'] | ['Crosslinked polyethylene (XLPE)'] | ['Red or yellow or blue or black or natural'] | ['PVC Type ST - 2 as per IS 5831 (Option: FR Type / FRLS Type)']
[9 empty] | 16 |  |  |  |  | 11 | [62 empty] | 111300100016 | 0.7 | 1.8 | 125 | 225
[9 empty] | 25 |  |  |  |  | 12 | [62 empty] | 111300100025 | 0.9 | 1.8 | 170 | 330
[9 empty] | 35 |  |  |  |  | 13 | [62 empty] | 111300100035 | 0.9 | 1.8 | 205 | 425
[9 empty] | 50 |  |  |  |  | 15 | [62 empty] | 111300100050 | 1 | 1.8 | 250 | 550
[9 empty] | 70 |  |  |  |  | 16 | [62 empty] | 111300100070 | 1.1 | 1.8 | 335 | 750
[9 empty] | 95 |  |  |  |  | 18 | [62 empty] | 111300100095 | 1.1 | 1.8 | 425 | 1000
[9 empty] | 120 |  |  |  |  | 20 | [62 empty] | 111300100120 | 1.2 | 1.8 | 515 | 1250
[9 empty] | 150 |  |  |  |  | 22 | [62 empty] | 111300100150 | 1.4 | 2 | 615 | 1520
[9 empty] | 185 |  |  |  |  | 24 | [62 empty] | 111300100185 | 1.6 | 2 | 770 | 1880
[9 empty] | 240 |  |  |  |  | 27 | [62 empty] | 111300100240 | 1.7 | 2 | 965 | 2415
[9 empty] | 300 |  |  |  |  | 30 | [62 empty] | 111300100300 | 1.8 | 2 | 1160 | 2980
[9 empty] | 400 |  |  |  |  | 33 | [62 empty] | 111300100400 | 2 | 2.2 | 1480 | 3800
[9 empty] | 500 |  |  |  |  | 36 | [62 empty] | 111300100500 | 2.2 | 2.2 | 1840 | 4815
[9 empty] | 630 |  |  |  |  | 40 | [62 empty] | 111300100630 | 2.4 | 2.2 | 2350 | 6150
[9 empty] | 800 |  |  |  |  | 47 | [62 empty] | 111300100800 | 2.6 | 2.4 | 2830 | 7840
[9 empty] | 1000 |  |  |  |  | 51 | [62 empty] | 111300101000 | 2.8 | 2.6 | 3670 | 9800
https://www.rrkabel.com/power-cables/power-cables-a2xy2xy-2-core | A2XY/2XY-2 CORE | ['https://www.rrkabel.com/Uploads/Products/115/ProductZoomForMoreDetailsImage/aluminium-A2XY-2XY-2-Core.jpg', 'https://www.rrkabel.com/Uploads/Products/115/ProductZoomImage/03-.jpg', 'https://www.rrkabel.com/Uploads/Products/343/ProductFeaturesDetails/01.png', 'https://www.rrkabel.com/Uploads/Products/343/ProductFeaturesDetails/01.png'] | ['1.1 kV (A.C) & 1.5 kV (D.C ) to Earth', '2 cores AL / CU conductor, XLPE insulated, unarmoured cables as per IS 7098 Part - 1.'] | ['AL up to 10 Sq. mm conductor are solid Cl. 1 as per IS 8130. And above 10 Sq. mm conductor are stranded round or compact round or compact shape conductor Cl. 2 as per'] | ['Crosslinked polyethylene (XLPE)'] | ['Red, black'] | ['PVC Type ST - 2 as per IS 5831 (Option : FR Type / FRLS Type)'] | [9 empty] | ['PVC / PVC tape as per IS 7098 (P - 1)'] | [64 empty] | ['8130', 'In CU 4 & 6 Sq. mm conductor are solid Cl. 1 or stranded round Cl. 2 as per IS:8130. 10 Sq. mm conductor is stranded round or stranded compact conductor Cl. 2 as per IS 8130', 'Above 10 Sq. mm conductor are stranded round or compact round or compacted shaped Cl. 2 as per : IS 8130']
[12 empty] | 0.7 | [5 empty] | 0.3 | 4 | [57 empty] | 111400200004 |  |  | 180 | 235 |  | 1.8 | 13
[12 empty] | 0.7 | [5 empty] | 0.3 | 6 | [57 empty] | 111400200006 |  |  | 220 | 300 |  | 1.8 | 14
[12 empty] | 0.7 | [5 empty] | 0.3 | 10 | [57 empty] | 111400200010 |  |  | 280 | 400 |  | 1.8 | 17
[12 empty] | 0.7 | [5 empty] | 0.3 | 16 | [57 empty] | 111400200016 |  |  | 300 | 440 |  | 1.8 | 17
[12 empty] | 0.9 | [5 empty] | 0.3 | 25 | [57 empty] | 111400200025 |  |  | 340 | 650 |  | 2 | 19
[12 empty] | 0.9 | [5 empty] | 0.3 | 35 | [57 empty] | 111400200035 |  |  | 415 | 840 |  | 2 | 20
[12 empty] | 1 | [5 empty] | 0.3 | 50 | [57 empty] | 111400200050 |  |  | 520 | 1090 |  | 2 | 22
[12 empty] | 1.1 | [5 empty] | 0.3 | 70 | [57 empty] | 111400200070 |  |  | 680 | 1500 |  | 2 | 25
[12 empty] | 1.1 | [5 empty] | 0.4 | 95 | [57 empty] | 111400200095 |  |  | 880 | 2010 |  | 2.2 | 28
[12 empty] | 1.2 | [5 empty] | 0.4 | 120 | [57 empty] | 111400200120 |  |  | 1080 | 2500 |  | 2.2 | 31
[12 empty] | 1.4 | [5 empty] | 0.4 | 150 | [57 empty] | 111400200150 |  |  | 1295 | 3060 |  | 2.2 | 33
[12 empty] | 1.6 | [5 empty] | 0.5 | 185 | [57 empty] | 111400200185 |  |  | 1630 | 3840 |  | 2.4 | 37
[12 empty] | 1.7 | [5 empty] | 0.5 | 240 | [57 empty] | 111400200240 |  |  | 2070 | 4970 |  | 2.6 | 41
[12 empty] | 1.8 | [5 empty] | 0.6 | 300 | [57 empty] | 111400200300 |  |  | 2520 | 6160 |  | 2.8 | 44
[12 empty] | 2 | [5 empty] | 0.6 | 400 | [57 empty] | 111400200400 |  |  | 3200 | 7830 |  | 3 | 48
[12 empty] | 2.2 | [5 empty] | 0.7 | 500 | [57 empty] | 111400200500 |  |  | 4040 | 9990 |  | 3.4 | 54
[12 empty] | 2.4 | [5 empty] | 0.7 | 630 | [57 empty] | 111400200630 |  |  | 5130 | 12840 |  | 3.6 | 62
https://www.rrkabel.com/power-cables/power-cables-a2xy2xy-3-core | A2XY/2XY-3 CORE | ['https://www.rrkabel.com/Uploads/Products/116/ProductZoomForMoreDetailsImage/copper-A2XY-2XY-3-Core.jpg', 'https://www.rrkabel.com/Uploads/Products/116/ProductZoomImage/03-.jpg', 'https://www.rrkabel.com/Uploads/Products/346/ProductFeaturesDetails/01.png', 'https://www.rrkabel.com/Uploads/Products/346/ProductFeaturesDetails/01.png'] | ['1.1 kV (A.C) & 1.5 kV (D.C ) to Earth', '3 Cores AL / CU conductor, XLPE insulated, unarmoured cables as per IS 7098 Part - 1.'] | ['AL up to 10 Sq. mm conductor are solid Cl.1 as per IS 8130. And above 10 Sq. mm conductor are stranded compacted shape Cl. 2 as per IS 8130', 'In CU 4 & 6 Sq. mm conductor are solid Cl. 1 or stranded Cl. 2 as per IS 8130. 10 Sq. mm conductor is stranded Cl. 2 round as per IS 8130. Above 10 Sq. mm conductor are stranded compacted shaped Cl. 2 as per IS 8130'] | ['Crosslinked polyethylene (XLPE)'] | ['Red, yellow, blue'] | ['PVC Type ST - 2 as per IS 5831 (Option : FR Type / FRLS Type)'] | [9 empty] | ['PVC / PVC tape as per IS 7098 (P - 1)']
[9 empty] | 4 |  |  |  |  | 14 | [5 empty] | 0.3 | [56 empty] | 111500300004 | 0.7 | 1.8 | 170 | 240
[9 empty] | 6 |  |  |  |  | 16 | [5 empty] | 0.3 | [56 empty] | 111500300006 | 0.7 | 1.8 | 200 | 300
[9 empty] | 10 |  |  |  |  | 18 | [5 empty] | 0.3 | [56 empty] | 111500300010 | 0.7 | 1.8 | 250 | 430
[9 empty] | 16 |  |  |  |  | 18 | [5 empty] | 0.3 | [56 empty] | 111500300016 | 0.7 | 1.8 | 310 | 600
[9 empty] | 25 |  |  |  |  | 21 | [5 empty] | 0.3 | [56 empty] | 111500300025 | 0.9 | 2 | 470 | 920
[9 empty] | 35 |  |  |  |  | 22 | [5 empty] | 0.3 | [56 empty] | 111500300035 | 0.9 | 2 | 570 | 1210
[9 empty] | 50 |  |  |  |  | 25 | [5 empty] | 0.3 | [56 empty] | 111500300050 | 1 | 2 | 720 | 1590
[9 empty] | 70 |  |  |  |  | 30 | [5 empty] | 0.4 | [56 empty] | 111500300070 | 1.1 | 2.2 | 950 | 2200
[9 empty] | 95 |  |  |  |  | 32 | [5 empty] | 0.4 | [56 empty] | 111500300095 | 1.1 | 2.2 | 1250 | 2980
[9 empty] | 120 |  |  |  |  | 35 | [5 empty] | 0.4 | [56 empty] | 111500300120 | 1.2 | 2.2 | 1520 | 3720
[9 empty] | 150 |  |  |  |  | 39 | [5 empty] | 0.5 | [56 empty] | 111500300150 | 1.4 | 2.4 | 1840 | 4550
[9 empty] | 185 |  |  |  |  | 43 | [5 empty] | 0.5 | [56 empty] | 111500300185 | 1.6 | 2.6 | 2310 | 5700
[9 empty] | 240 |  |  |  |  | 49 | [5 empty] | 0.6 | [56 empty] | 111500300240 | 1.7 | 2.8 | 3010 | 7390
[9 empty] | 300 |  |  |  |  | 53 | [5 empty] | 0.6 | [56 empty] | 111500300300 | 1.8 | 3 | 3600 | 9190
[9 empty] | 400 |  |  |  |  | 59 | [5 empty] | 0.7 | [56 empty] | 111500300400 | 2 | 3.2 | 4560 | 11700
[9 empty] | 500 |  |  |  |  | 66 | [5 empty] | 0.7 | [56 empty] | 111500300500 | 2.2 | 3.6 | 5780 | 14940
[9 empty] | 630 |  |  |  |  | 73 | [5 empty] | 0.7 | [56 empty] | 111500300630 | 2.4 | 3.8 | 7360 | 19230
https://www.rrkabel.com/power-cables/power-cables-a2xy2xy-3-5-core | A2XY/2XY-3.5 CORE | ['https://www.rrkabel.com/Uploads/Products/117/ProductZoomForMoreDetailsImage/aluminium-A2XY-2XY-3.5-Core.jpg', 'https://www.rrkabel.com/Uploads/Products/117/ProductZoomImage/03-.jpg', 'https://www.rrkabel.com/Uploads/Products/349/ProductFeaturesDetails/01.png', 'https://www.rrkabel.com/Uploads/Products/349/ProductFeaturesDetails/01.png'] | ['1.1 kV (A.C) & 1.5 kV (D.C ) to Earth', '3.5 Cores AL / CU Conductor, XLPE Insulated, Unarmoured Cables as per IS:7098 Part-1. Conductor : AL / CU Stranded compact shaped conductor as per Cl. 2, IS:8130 Insulation : Crosslinked polyethylene (XLPE)'] |  |  |  | ['PVC Type ST-2 as per IS:5831 (Option: FR Type / FRLS Type)'] | [9 empty] | ['PVC / PVC tape as per IS:7098 (P-1)'] | [43 empty] | ['Red, yellow, blue'] | ['Black']
[9 empty] | 3×25+16 |  |  |  |  | 22 | [5 empty] | 0.3 | [56 empty] | 111601010211 | 0.9/0.7 | 2 | 575 | 1125
[9 empty] | 3×35+16 |  |  |  |  | 24 | [5 empty] | 0.3 | [56 empty] | 111601020211 | 0.9/0.7 | 2 | 685 | 1425
[9 empty] | 3×50+25 |  |  |  |  | 27 | [5 empty] | 0.3 | [56 empty] | 111601030211 | 1.0/0.9 | 2 | 880 | 1980
[9 empty] | 3×70+35 |  |  |  |  | 31 | [5 empty] | 0.4 | [56 empty] | 111601040211 | 1.1/0.9 | 2.2 | 1185 | 2680
[9 empty] | 3×95+50 |  |  |  |  | 34 | [5 empty] | 0.4 | [56 empty] | 111601050211 | 1.1/1.0 | 2.2 | 1480 | 3580
[9 empty] | 3×120+70 |  |  |  |  | 38 | [5 empty] | 0.4 | [56 empty] | 111601060211 | 1.2/1.1 | 2.2 | 1880 | 4480
[9 empty] | 3×150+70 |  |  |  |  | 43 | [5 empty] | 0.5 | [56 empty] | 111601070211 | 1.4/1.1 | 2.4 | 2275 | 5485
[9 empty] | 3×185+95 |  |  |  |  | 46 | [5 empty] | 0.5 | [56 empty] | 111601080211 | 1.6/1.1 | 2.6 | 2770 | 6785
[9 empty] | 3×240+120 |  |  |  |  | 52 | [5 empty] | 0.6 | [56 empty] | 111601090211 | 1.7/1.2 | 2.8 | 3580 | 8675
[9 empty] | 3×300+150 |  |  |  |  | 57 | [5 empty] | 0.6 | [56 empty] | 111601100211 | 1.8/1.4 | 3 | 4380 | 10780
[9 empty] | 3×400+185 |  |  |  |  | 65 | [5 empty] | 0.7 | [56 empty] | 111601110211 | 2.0/1.6 | 3.4 | 5580 | 13980
[9 empty] | 3×500+240 |  |  |  |  | 73 | [5 empty] | 0.7 | [56 empty] | 111601120211 | 2.2/1.7 | 3.6 | 6980 | 17425
[9 empty] | 3×630+300 |  |  |  |  | 82 | [5 empty] | 0.7 | [56 empty] | 111601130211 | 2.4/1.8 | 4 | 8885 | 21970
https://www.rrkabel.com/power-cables/power-cables-a2xy2xy-4-core | A2XY/2XY-4 CORE | ['https://www.rrkabel.com/Uploads/Products/118/ProductZoomForMoreDetailsImage/copper-A2XY-2XY-4-Core.jpg', 'https://www.rrkabel.com/Uploads/Products/118/ProductZoomImage/03-.jpg', 'https://www.rrkabel.com/Uploads/Products/352/ProductFeaturesDetails/01.png', 'https://www.rrkabel.com/Uploads/Products/352/ProductFeaturesDetails/01.png'] | ['1.1 kV (A.C) & 1.5 kV (D.C ) to Earth', '4 cores AL /CU conductor, XLPE insulated, unarmoured cables as per IS 7098 Part - 1.'] | ['AL up to 10 Sq. mm conductor are solid Cl. 1 as per IS 8130. And above 10 Sq. mm conductor are stranded compacted shape Cl. 2 as per IS 8130', 'In CU 4 & 6 Sq. mm conductor are solid Cl. 1 or stranded Cl.2 as per IS 8130. 10 Sq. mm conductor is stranded Cl. 2 round as per IS 8130. Above 10 Sq. mm conductor are stranded compacted shaped Cl. 2 as per IS 8130'] | ['Crosslinked polyethylene (XLPE)'] | ['Red, yellow, blue, black'] | ['PVC Type ST - 2 as per IS 5831 (Option : FR Type / FRLS Type)'] | [9 empty] | ['PVC / PVC tape as per IS 7098 ( P - 1 )']
[9 empty] | 4 |  |  |  |  | 16 | [5 empty] | 0.3 | [56 empty] | 111700400004 | 0.7 | 1.8 | 225 | 340
[9 empty] | 6 |  |  |  |  | 17 | [5 empty] | 0.3 | [56 empty] | 111700400006 | 0.7 | 1.8 | 315 | 480
[9 empty] | 10 |  |  |  |  | 19 | [5 empty] | 0.3 | [56 empty] | 111700400010 | 0.7 | 1.8 | 370 | 640
[9 empty] | 16 |  |  |  |  | 20 | [5 empty] | 0.3 | [56 empty] | 111700400016 | 0.7 | 1.8 | 440 | 840
[9 empty] | 25 |  |  |  |  | 24 | [5 empty] | 0.3 | [56 empty] | 111700400025 | 0.9 | 2 | 650 | 1290
[9 empty] | 35 |  |  |  |  | 26 | [5 empty] | 0.3 | [56 empty] | 111700400035 | 0.9 | 2 | 780 | 1685
[9 empty] | 50 |  |  |  |  | 29 | [5 empty] | 0.3 | [56 empty] | 111700400050 | 1 | 2 | 985 | 2190
[9 empty] | 70 |  |  |  |  | 34 | [5 empty] | 0.4 | [56 empty] | 111700400070 | 1.1 | 2.2 | 1380 | 3090
[9 empty] | 95 |  |  |  |  | 37 | [5 empty] | 0.4 | [56 empty] | 111700400095 | 1.1 | 2.2 | 1685 | 3980
[9 empty] | 120 |  |  |  |  | 41 | [5 empty] | 0.5 | [56 empty] | 111700400120 | 1.2 | 2.4 | 2125 | 5130
[9 empty] | 150 |  |  |  |  | 45 | [5 empty] | 0.5 | [56 empty] | 111700400150 | 1.4 | 2.6 | 2630 | 6230
[9 empty] | 185 |  |  |  |  | 50 | [5 empty] | 0.5 | [56 empty] | 111700400185 | 1.6 | 2.8 | 3230 | 7830
[9 empty] | 240 |  |  |  |  | 56 | [5 empty] | 0.6 | [56 empty] | 111700400240 | 1.7 | 3 | 4080 | 9980
[9 empty] | 300 |  |  |  |  | 63 | [5 empty] | 0.7 | [56 empty] | 111700400300 | 1.8 | 3.2 | 5030 | 12030
[9 empty] | 400 |  |  |  |  | 70 | [5 empty] | 0.7 | [56 empty] | 111700400400 | 2 | 3.6 | 6385 | 15980
[9 empty] | 500 |  |  |  |  | 79 | [5 empty] | 0.7 | [56 empty] | 111700400500 | 2.2 | 3.8 | 7980 | 19985
[9 empty] | 630 |  |  |  |  | 88 | [5 empty] | 0.7 | [56 empty] | 111700400630 | 2.4 | 4 | 9985 | 25985
https://www.rrkabel.com/power-cables/power-cables-a2xfay2xfay-a2xway2xway | A2XFaY/2XFaY-A2XWaY/2XWaY | ['https://www.rrkabel.com/Uploads/Products/119/ProductZoomForMoreDetailsImage/aluminium-A2XFaY-2XFaY-A2XWaY-2XWaY.jpg', 'https://www.rrkabel.com/Uploads/Products/119/ProductZoomImage/03-.jpg', 'https://www.rrkabel.com/Uploads/Products/355/ProductFeaturesDetails/01.png', 'https://www.rrkabel.com/Uploads/Products/355/ProductFeaturesDetails/01.png'] | ['1.1 kV (A.C) & 1.5 kV (D.C ) to Earth', '1 cores AL / CU conductor, XLPE insulated, aluminum strip / wire armoured cables as per IS 7098 Part - 1.'] | ['AL up to 10 Sq. mm conductor are solid Cl. 1 as per IS 8130. And above 10 Sq. mm conductor are stranded round or compact Cl. 2 as per IS 8130', 'In CU 4 & 6 Sq. mm conductor are solid Cl. 1 or stranded Cl. 2 as per IS 8130. 10 Sq. mm & above stranded round or stranded compact Cl. 2 as per IS 8130'] | ['Crosslinked polyethylene (XLPE)'] | ['Red or yellow or blue or black'] | ['PVC Type ST - 2 as per IS 5831 (Option : FR Type / FRLS Type)'] | [18 empty] | ['Single armouring of aluminium strip or aluminium wire as per IS 7098 P - 1']
[28 empty] | 111800100016 | 16 | [55 empty] | 1 | [5 empty] | 1.4 | 1.24 | 13 | 200 | 300
[28 empty] | 111800100025 | 25 | [55 empty] | 1.2 | [5 empty] | 1.4 | 1.24 | 14 | 300 | 455
[28 empty] | 111800100035 | 35 | [55 empty] | 1.2 | [5 empty] | 1.4 | 1.24 | 15 | 350 | 567
[28 empty] | 111800100050 | 50 | [55 empty] | 1.3 | [5 empty] | 1.4 | 1.24 | 17 | 420 | 730
[28 empty] | 111800100070 | 70 | [55 empty] | 1.4 | [5 empty] | 1.4 | 1.24 | 19 | 520 | 954
[28 empty] | 111800100095 | 95 | [55 empty] | 1.4 | 0.8 | 1.4 | 21 | 600 | 1195 | 1.6 | 1.4 | 22 | 650 | 1235
[28 empty] | 111800100120 | 120 | [55 empty] | 1.5 | 0.8 | 1.4 | 23 | 700 | 1450 | 1.6 | 1.4 | 24 | 750 | 1494
[28 empty] | 111800100150 | 150 | [55 empty] | 1.7 | 0.8 | 1.4 | 24 | 800 | 1730 | 1.6 | 1.4 | 25 | 850 | 1780
[28 empty] | 111800100185 | 185 | [55 empty] | 1.9 | 0.8 | 1.4 | 26 | 950 | 2100 | 1.6 | 1.4 | 28 | 1000 | 2147
[28 empty] | 111800100240 | 240 | [55 empty] | 2 | 0.8 | 1.4 | 30 | 1200 | 2690 | 1.6 | 1.4 | 30 | 1250 | 2738
[28 empty] | 111800100300 | 300 | [55 empty] | 2.1 | 0.8 | 1.56 | 32 | 1400 | 3270 | 1.6 | 1.56 | 33 | 1500 | 3360
[28 empty] | 111800100400 | 400 | [55 empty] | 2.4 | 0.8 | 1.56 | 36 | 1750 | 4230 | 2 | 1.56 | 38 | 1900 | 4380
[28 empty] | 111800100500 | 500 | [55 empty] | 2.6 | 0.8 | 1.56 | 39 | 2150 | 5250 | 2 | 1.56 | 41 | 2350 | 5450
[28 empty] | 111800100630 | 630 | [55 empty] | 2.8 | 0.8 | 1.72 | 44 | 2700 | 6610 | 2 | 1.72 | 46 | 2900 | 6806
[28 empty] | 111800100800 | 800 | [55 empty] | 3.1 | 0.8 | 1.72 | 48 | 3350 | 8320 | 2 | 1.88 | 51 | 3600 | 8560
[28 empty] | 111800101000 | 1000 | [55 empty] | 3.3 | 0.8 | 1.88 | 54 | 4100 | 10300 | 2.5 | 2.04 | 56 | 4600 | 10800
https://www.rrkabel.com/power-cables/power-cables-a2xfy2xfy-a2xwy2xwy-2-core | A2XFY/2XFY-A2XWY/2XWY-2 CORE | ['https://www.rrkabel.com/Uploads/Products/120/ProductZoomForMoreDetailsImage/copper-A2XFY-2XFY-A2XWY-2XWY-2-Cores.jpg', 'https://www.rrkabel.com/Uploads/Products/120/ProductZoomImage/03-.jpg', 'https://www.rrkabel.com/Uploads/Products/358/ProductFeaturesDetails/01.png', 'https://www.rrkabel.com/Uploads/Products/358/ProductFeaturesDetails/01.png'] | ['1.1 kV (A.C) & 1.5 kV (D.C ) to Earth', '2 cores AL / CU conductor, XLPE insulated, galvanised steel strip / wire armoured cables as per IS 7098 Part - 1.'] | ['AL up to 10 Sq. mm conductor are solid Cl. 1 as per IS 8130. And above 10 Sq. mm conductor are stranded round or compact round or compact shape conductor Cl. 2 as per IS 8130', 'In CU 4 & 6 Sq. mm conductor are solid Cl. 1 or stranded round Cl. 2 as per IS 8130. 10 Sq. mm conductor is stranded round or stranded compact conductor Cl. 2 as per IS 8130', 'Above 10 Sq. mm conductor are stranded round or compact round or compacted shaped Cl. 2 as per IS 8130'] | ['Crosslinked polyethylene (XLPE)'] | ['Red, black'] | [10 empty] | ['PVC / PVC tape as per IS 7098 ( P-1 )']
[28 empty] | 111900200004 | 4 | [55 empty] | 0.7 | [5 empty] | 1.4 | 1.24 | 15 | 500 | 550 | 0.3
[28 empty] | 111900200006 | 6 | [55 empty] | 0.7 | [5 empty] | 1.4 | 1.24 | 16 | 550 | 600 | 0.3
[28 empty] | 111900200010 | 10 | [55 empty] | 0.7 | [5 empty] | 1.4 | 1.24 | 18 | 650 | 770 | 0.3
[28 empty] | 111900200016 | 16 | [55 empty] | 0.7 | [5 empty] | 1.4 | 1.4 | 19 | 700 | 900 | 0.3
[28 empty] | 111900200025 | 25 | [55 empty] | 0.9 | 0.8 | 1.4 | 20 | 650 | 950 | 1.6 | 1.4 | 21 | 850 | 1150 | 0.3
[28 empty] | 111900200035 | 35 | [55 empty] | 0.9 | 0.8 | 1.4 | 21 | 750 | 1200 | 1.6 | 1.4 | 23 | 950 | 1400 | 0.3
[28 empty] | 111900200050 | 50 | [55 empty] | 1 | 0.8 | 1.4 | 23 | 900 | 1500 | 1.6 | 1.4 | 25 | 1100 | 1700 | 0.3
[28 empty] | 111900200070 | 70 | [55 empty] | 1.1 | 0.8 | 1.56 | 26 | 1100 | 1950 | 1.6 | 1.56 | 28 | 1400 | 2250 | 0.3
[28 empty] | 111900200095 | 95 | [55 empty] | 1.1 | 0.8 | 1.56 | 29 | 1350 | 2500 | 2 | 1.56 | 31 | 1850 | 3000 | 0.4
[28 empty] | 111900200120 | 120 | [55 empty] | 1.2 | 0.8 | 1.56 | 31 | 1600 | 3100 | 2 | 1.56 | 34 | 2150 | 3600 | 0.4
[28 empty] | 111900200150 | 150 | [55 empty] | 1.4 | 0.8 | 1.72 | 34 | 1900 | 3750 | 2 | 1.72 | 37 | 2450 | 4300 | 0.4
[28 empty] | 111900200185 | 185 | [55 empty] | 1.6 | 0.8 | 1.72 | 37 | 2250 | 4500 | 2 | 1.88 | 40 | 2900 | 5200 | 0.5
[28 empty] | 111900200240 | 240 | [55 empty] | 1.7 | 0.8 | 1.88 | 42 | 2800 | 5800 | 2.5 | 2.04 | 45 | 3850 | 6800 | 0.5
[28 empty] | 111900200300 | 300 | [55 empty] | 1.8 | 0.8 | 2.04 | 45 | 3300 | 7000 | 2.5 | 2.2 | 49 | 4450 | 8200 | 0.6
[28 empty] | 111900200400 | 400 | [55 empty] | 2 | 0.8 | 2.36 | 50 | 4100 | 9050 | 2.5 | 2.36 | 52 | 5350 | 10300 | 0.6
[28 empty] | 111900200500 | 500 | [55 empty] | 2.2 | 0.8 | 2.52 | 55 | 5000 | 11000 | 3.2 | 2.68 | 60 | 7100 | 13300 | 0.7
[28 empty] | 111900200630 | 630 | [55 empty] | 2.4 | 0.8 | 2.68 | 63 | 6100 | 14000 | 3.2 | 2.84 | 66 | 8500 | 16300 | 0.7
https://www.rrkabel.com/power-cables/power-cables-a2xfy2xfy-a2xwy2xwy-3-core | A2XFY/2XFY-A2XWY/2XWY-3 CORE | ['https://www.rrkabel.com/Uploads/Products/121/ProductZoomForMoreDetailsImage/aluminium-A2XFY-2XFY-A2XWY-2XWY-3-Cores.jpg', 'https://www.rrkabel.com/Uploads/Products/121/ProductZoomImage/03-.jpg', 'https://www.rrkabel.com/Uploads/Products/361/ProductFeaturesDetails/01.png', 'https://www.rrkabel.com/Uploads/Products/361/ProductFeaturesDetails/01.png'] | ['1.1 kV (A.C) & 1.5 kV (D.C ) to Earth', '3 cores AL /CU conductor, XLPE insulated, galvanised steel strip /wire armoured cables as per IS 7098 Part -1.'] | ['AL up to 10 Sq. mm conductor are solid Cl. 1 as per IS 8130. And above 10 Sq. mm conductor are stranded compacted shape Cl. 2 as per IS 8130.', 'In CU 4 & 6 Sq. mm conductor are solid Cl. 1 or stranded Cl. 2 as per IS 8130. 10 Sq. mm conductor is stranded Cl. 2,round as per IS 8130. Above 10 Sq. mm conductor are stranded compacted shaped Cl. 2 as per IS 8130.'] | ['Crosslinked polyethylene (XLPE)'] | ['Red, yellow, blue'] | ['PVC Type ST - 2 as per IS 5831. (Option : FR Type / FRLS Type)'] | [9 empty] | ['PVC / PVC tape as per IS 7098 (P - 1)'] | [8 empty] | ['Single armouring of galvanised steel strip / wire']
[28 empty] | 112000300004 | 4 | [55 empty] | 0.7 | [5 empty] | 1.4 | 1.24 | 18 | 430 | 510 | 0.3
[28 empty] | 112000300006 | 6 | [55 empty] | 0.7 | [5 empty] | 1.4 | 1.24 | 19 | 470 | 600 | 0.3
[28 empty] | 112000300010 | 10 | [55 empty] | 0.7 | [5 empty] | 1.4 | 1.24 | 20 | 520 | 750 | 0.3
[28 empty] | 112000300016 | 16 | [55 empty] | 0.7 | 0.8 | 1.24 | 19 | 590 | 890 | 1.6 | 1.4 | 20 | 730 | 1020 | 0.3
[28 empty] | 112000300025 | 25 | [55 empty] | 0.9 | 0.8 | 1.4 | 21 | 790 | 1190 | 1.6 | 1.4 | 23 | 940 | 1400 | 0.3
[28 empty] | 112000300035 | 35 | [55 empty] | 0.9 | 0.8 | 1.4 | 23 | 940 | 1490 | 1.6 | 1.4 | 25 | 1130 | 1750 | 0.3
[28 empty] | 112000300050 | 50 | [55 empty] | 1 | 0.8 | 1.4 | 26 | 1090 | 1990 | 1.6 | 1.56 | 29 | 1330 | 2180 | 0.3
[28 empty] | 112000300070 | 70 | [55 empty] | 1.1 | 0.8 | 1.56 | 29 | 1450 | 2690 | 2 | 1.56 | 32 | 1820 | 3070 | 0.4
[28 empty] | 112000300095 | 95 | [55 empty] | 1.1 | 0.8 | 1.56 | 32 | 1740 | 3490 | 2 | 1.56 | 35 | 2210 | 3950 | 0.4
[28 empty] | 112000300120 | 120 | [55 empty] | 1.2 | 0.8 | 1.56 | 35 | 2100 | 4190 | 2 | 1.72 | 39 | 2670 | 4840 | 0.4
[28 empty] | 112000300150 | 150 | [55 empty] | 1.4 | 0.8 | 1.72 | 42 | 2520 | 5200 | 2 | 1.88 | 43 | 3450 | 6150 | 0.5
[28 empty] | 112000300185 | 185 | [55 empty] | 1.6 | 0.8 | 1.88 | 44 | 2990 | 6300 | 2.5 | 2.04 | 48 | 3830 | 7160 | 0.5
[28 empty] | 112000300240 | 240 | [55 empty] | 1.7 | 0.8 | 2.04 | 49 | 3740 | 8190 | 2.5 | 2.2 | 53 | 4720 | 8870 | 0.6
[28 empty] | 112000300300 | 300 | [55 empty] | 1.8 | 0.8 | 2.2 | 54 | 4490 | 10000 | 2.5 | 2.36 | 58 | 6130 | 11380 | 0.6
[28 empty] | 112000300400 | 400 | [55 empty] | 2 | 0.8 | 2.52 | 60 | 5590 | 12990 | 3.2 | 2.68 | 65 | 7390 | 14410 | 0.7
[28 empty] | 112000300500 | 500 | [55 empty] | 2.2 | 0.8 | 2.68 | 66 | 6890 | 15990 | 3.2 | 2.84 | 72 | 9980 | 18490 | 0.7
[28 empty] | 112000300630 | 630 | [55 empty] | 2.4 | 0.8 | 2.84 | 74 | 8540 | 19990 | 4 | 3 | 81 | 11820 | 22560 | 0.7
https://www.rrkabel.com/power-cables/power-cables-a2xfy2xfy-a2xwy2xwy-3-5-core | A2XFY/2XFY-A2XWY/2XWY-3.5 CORE | ['https://www.rrkabel.com/Uploads/Products/122/ProductZoomForMoreDetailsImage/copper-A2XFY-2XFY-A2XWY-2XWY-3.5-Cores.jpg', 'https://www.rrkabel.com/Uploads/Products/122/ProductZoomImage/03-.jpg', 'https://www.rrkabel.com/Uploads/Products/364/ProductFeaturesDetails/01.png', 'https://www.rrkabel.com/Uploads/Products/364/ProductFeaturesDetails/01.png'] | ['1.1 kV (A.C) & 1.5 kV (D.C ) to Earth', '3.5 cores AL / CU conductor, XLPE insulated, galvanised steel strip / wire armoured Cables as per IS 7098 Part -1.'] | ['AL / CU stranded compact shaped conductor as per Cl. 2, IS 8130.'] | ['Crosslinked polyethylene (XLPE)'] |  | ['PVC Type ST - 2 as per IS 5831. (Option : FR Type / FRLS Type)'] | [9 empty] | ['PVC / PVC tape as per IS 7098 (P - 1)'] | [8 empty] | ['Single armouring of galvanised steel strip / wire'] | [34 empty] | ['Red, yellow, blue'] | ['Black']
[28 empty] | 112101010211 |  |  |  | 0.9/0.7 | [63 empty] | 0.3 | 3×25+16 | 0.8 | 1.4 | 23 | 900 | 1400 | 1.6 | 1.4 | 25 | 1080 | 1685
[28 empty] | 112101020211 |  |  |  | 0.9/0.7 | [63 empty] | 0.3 | 3×35+16 | 0.8 | 1.4 | 25 | 1000 | 1800 | 1.6 | 1.4 | 27 | 1285 | 1980
[28 empty] | 112101030211 |  |  |  | 1.0/0.9 | [63 empty] | 0.3 | 3×50+25 | 0.8 | 1.4 | 28 | 1200 | 2300 | 1.6 | 1.56 | 30 | 1580 | 2685
[28 empty] | 112101040211 |  |  |  | 1.1/0.9 | [63 empty] | 0.4 | 3×70+35 | 0.8 | 1.56 | 32 | 1600 | 3200 | 2 | 1.56 | 35 | 2190 | 3690
[28 empty] | 112101050211 |  |  |  | 1.1/1.0 | [63 empty] | 0.4 | 3×95+50 | 0.8 | 1.56 | 35 | 2000 | 4100 | 2 | 1.56 | 38 | 2580 | 4585
[28 empty] | 112101060211 |  |  |  | 1.2/1.1 | [63 empty] | 0.4 | 3×120+70 | 0.8 | 1.72 | 39 | 2400 | 5100 | 2 | 1.72 | 42 | 3085 | 5680
[28 empty] | 112101070211 |  |  |  | 1.4/1.1 | [63 empty] | 0.5 | 3×150+70 | 0.8 | 1.72 | 43 | 2800 | 6000 | 2 | 1.88 | 46 | 3590 | 6790
[28 empty] | 112101080211 |  |  |  | 1.6/1.1 | [63 empty] | 0.5 | 3×185+95 | 0.8 | 1.88 | 47 | 3400 | 7400 | 2.5 | 2.04 | 51 | 4675 | 8615
[28 empty] | 112101090211 |  |  |  | 1.7/1.2 | [63 empty] | 0.6 | 3×240+120 | 0.8 | 2.04 | 53 | 4300 | 9500 | 2.5 | 2.2 | 56 | 5680 | 10485
[28 empty] | 112101100211 |  |  |  | 1.8/1.4 | [63 empty] | 0.6 | 3×300+150 | 0.8 | 2.2 | 57 | 5000 | 11500 | 2.5 | 2.36 | 60 | 6685 | 12990
[28 empty] | 112101110211 |  |  |  | 2.0/1.6 | [63 empty] | 0.7 | 3×400+185 | 0.8 | 2.52 | 66 | 6400 | 14500 | 3.2 | 2.68 | 71 | 8980 | 16980
[28 empty] | 112101120211 |  |  |  | 2.2/1.7 | [63 empty] | 0.7 | 3×500+240 | 0.8 | 2.68 | 74 | 7900 | 18000 | 3.2 | 2.84 | 79 | 10985 | 21485
[28 empty] | 112101130211 |  |  |  | 2.4/1.8 | [63 empty] | 0.7 | 3×630+300 | 0.8 | 3 | 82 | 9900 | 23000 | 4 | 3 | 88 | 14490 | 27985
https://www.rrkabel.com/power-cables/power-cables-a2xfy2xfy-a2xwy2xwy-4-core | A2XFY/2XFY-A2XWY/2XWY-4 CORE | ['https://www.rrkabel.com/Uploads/Products/123/ProductZoomForMoreDetailsImage/aluminium-A2XFY-2XFY-A2XWY-2XWY-4-Cores.jpg', 'https://www.rrkabel.com/Uploads/Products/123/ProductZoomImage/03-.jpg', 'https://www.rrkabel.com/Uploads/Products/367/ProductFeaturesDetails/01.png', 'https://www.rrkabel.com/Uploads/Products/367/ProductFeaturesDetails/01.png'] | ['1.1 kV (A.C) & 1.5 kV (D.C ) to Earth', '4 cores AL / CU conductor, XLPE insulated, galvanised steel strip / wire armoured cables as per IS 7098 Part - 1.'] | ['AL up to 10 Sq. mm conductor are solid Cl. 1 as per IS 8130. And above 10 Sq. mm conductor are stranded compacted shape Cl. 2 as per IS 8130', 'In CU 4 & 6 Sq. mm conductor are solid Cl. 1 or stranded Cl. 2 as per IS 8130. 10 Sq. mm conductor is stranded Cl. 2, round as per IS 8130. Above 10 Sq. mm conductor are stranded compacted shaped Cl. 2 as per IS 8130'] | ['Crosslinked polyethylene (XLPE)'] | ['Red, yellow, blue, black'] | ['PVC Type ST - 2 as per IS 5831 (Option : FR Type / FRLS Type)'] | [9 empty] | ['PVC / PVC tape as per IS 7098 (P - 1)'] | [8 empty] | ['Single armouring of galvanised steel strip / wire']
[28 empty] | 112200400004 |  |  |  | 0.7 | [63 empty] | 0.3 | 4 | [5 empty] | 1.4 | 1.24 | 18 | 540 | 640
[28 empty] | 112200400006 |  |  |  | 0.7 | [63 empty] | 0.3 | 6 | [5 empty] | 1.4 | 1.24 | 19 | 590 | 760
[28 empty] | 112200400010 |  |  |  | 0.7 | [63 empty] | 0.3 | 10 | [5 empty] | 1.4 | 1.4 | 21 | 655 | 940
[28 empty] | 112200400016 |  |  |  | 0.7 | [63 empty] | 0.3 | 16 | 0.8 | 1.4 | 20 | 700 | 1100 | 1.6 | 1.4 | 22 | 920 | 1280
[28 empty] | 112200400025 |  |  |  | 0.9 | [63 empty] | 0.3 | 25 | 0.8 | 1.4 | 24 | 900 | 1500 | 1.6 | 1.4 | 26 | 1185 | 1750
[28 empty] | 112200400035 |  |  |  | 0.9 | [63 empty] | 0.3 | 35 | 0.8 | 1.4 | 27 | 1100 | 2000 | 1.6 | 1.4 | 28 | 1420 | 2185
[28 empty] | 112200400050 |  |  |  | 1 | [63 empty] | 0.3 | 50 | 0.8 | 1.56 | 30 | 1400 | 2500 | 1.6 | 1.56 | 32 | 1730 | 2830
[28 empty] | 112200400070 |  |  |  | 1.1 | [63 empty] | 0.4 | 70 | 0.8 | 1.56 | 34 | 1800 | 3400 | 2 | 1.56 | 37 | 2375 | 3980
[28 empty] | 112200400095 |  |  |  | 1.1 | [63 empty] | 0.4 | 95 | 0.8 | 1.56 | 37 | 2200 | 4400 | 2 | 1.72 | 40 | 2870 | 5130
[28 empty] | 112200400120 |  |  |  | 1.2 | [63 empty] | 0.5 | 120 | 0.8 | 1.72 | 41 | 2700 | 5600 | 2 | 1.88 | 44 | 3475 | 6285
[28 empty] | 112200400150 |  |  |  | 1.4 | [63 empty] | 0.5 | 150 | 0.8 | 1.88 | 46 | 3200 | 6800 | 2.5 | 2.04 | 49 | 4480 | 7980
[28 empty] | 112200400185 |  |  |  | 1.6 | [63 empty] | 0.5 | 185 | 0.8 | 2.04 | 51 | 3900 | 8300 | 2.5 | 2.2 | 54 | 5185 | 9680
[28 empty] | 112200400240 |  |  |  | 1.7 | [63 empty] | 0.6 | 240 | 0.8 | 2.2 | 57 | 4850 | 10500 | 2.5 | 2.36 | 65 | 6385 | 11985
[28 empty] | 112200400500 |  |  |  | 2.2 | [63 empty] | 0.7 | 500 | 0.8 | 2.84 | 79 | 9000 | 21000 | 4 | 3 | 86 | 13480 | 24985
[28 empty] | 112200400630 |  |  |  | 2.4 | [63 empty] | 0.7 | 630 | 0.8 | 3 | 88 | 11000 | 27000 | 4 | 3 | 94 | 15975 | 30485
https://www.rrkabel.com/power-cables/power-cables-2xy2xfy2xwy-1-5-sq-mm1 | 2XY/2XFY/2XWY-1.5 Sq. mm | ['https://www.rrkabel.com/Uploads/Products/124/ProductZoomForMoreDetailsImage/02.jpg', 'https://www.rrkabel.com/Uploads/Products/124/ProductZoomImage/last-03.jpg', 'https://www.rrkabel.com/Uploads/Products/370/ProductFeaturesDetails/01.png', 'https://www.rrkabel.com/Uploads/Products/370/ProductFeaturesDetails/01.png'] | ['1.5 Sq. mm copper conductor, XLPE insulated unarmoured & galvanised steel strip / wire armoured control cables as per IS 7098 Part - 1'] | ['CU Conductor solid as per Cl. 1 IS 8130 or Stranded as per Cl. 2 IS 8130'] | ['Crosslinked polyethylene ( XLPE )'] |  | ['PVC Type ST - 2 as per IS 5831 (Option : FR Type / FRLS Type)'] | [9 empty] | ['PVC / PVC tape as per IS 7098 (P - 1)'] | [8 empty] | ['Single armouring of galvanised steel strip / wire'] | [37 empty] | ['Up to 5 cores by colour coding & more than 5 cores number printing on core as per IS 7098 Part - 1']
[28 empty] | 112300201105 | [56 empty] | 0.7 | [10 empty] | 0.3 | [11 empty] | 2 | 1.8 | 10 | 140 |  |  |  |  | 1.4 | 1.24 | 12.5 | 370
[28 empty] | 112300301105 | [56 empty] | 0.7 | [10 empty] | 0.3 | [11 empty] | 3 | 1.8 | 10.5 | 160 |  |  |  |  | 1.4 | 1.24 | 13 | 390
[28 empty] | 112300401105 | [56 empty] | 0.7 | [10 empty] | 0.3 | [11 empty] | 4 | 1.8 | 11.5 | 200 |  |  |  |  | 1.4 | 1.24 | 13.5 | 415
[28 empty] | 112300501105 | [56 empty] | 0.7 | [10 empty] | 0.3 | [11 empty] | 5 | 1.8 | 12.5 | 225 |  |  |  |  | 1.4 | 1.24 | 14.5 | 465
[28 empty] | 112300601105 | [56 empty] | 0.7 | [10 empty] | 0.3 | [11 empty] | 6 | 1.8 | 13.5 | 250 |  |  |  |  | 1.4 | 1.24 | 15.5 | 500
[28 empty] | 112300701105 | [56 empty] | 0.7 | [10 empty] | 0.3 | [11 empty] | 7 | 1.8 | 13.5 | 260 |  |  |  |  | 1.4 | 1.24 | 15.5 | 520
[28 empty] | 112301001105 | [56 empty] | 0.7 | [10 empty] | 0.3 | [11 empty] | 10 | 1.8 | 17 | 340 |  |  |  |  | 1.4 | 1.24 | 18.5 | 655
[28 empty] | 112301201105 | [56 empty] | 0.7 | [10 empty] | 0.3 | [11 empty] | 12 | 1.8 | 17.5 | 390 |  |  |  |  | 1.6 | 1.4 | 19 | 720
[28 empty] | 112301401105 | [56 empty] | 0.7 | [10 empty] | 0.3 | [11 empty] | 14 | 1.8 | 18 | 430 |  |  |  |  | 1.6 | 1.4 | 20 | 825
[28 empty] | 112301601105 | [56 empty] | 0.7 | [10 empty] | 0.3 | [11 empty] | 16 | 1.8 | 18.5 | 475 | 0.8 | 1.4 | 19 | 750 | 1.6 | 1.4 | 21 | 925
[28 empty] | 112301901105 | [56 empty] | 0.7 | [10 empty] | 0.3 | [11 empty] | 19 | 2 | 19.5 | 540 | 0.8 | 1.4 | 20 | 815 | 1.6 | 1.4 | 22 | 1010
[28 empty] | 112302401105 | [56 empty] | 0.7 | [10 empty] | 0.3 | [11 empty] | 24 | 2 | 22.5 | 665 | 0.8 | 1.4 | 23 | 1000 | 1.6 | 1.4 | 25 | 1250
[28 empty] | 112302701105 | [56 empty] | 0.7 | [10 empty] | 0.3 | [11 empty] | 27 | 2 | 23 | 750 | 0.8 | 1.4 | 23.5 | 1050 | 1.6 | 1.4 | 25.5 | 1330
[28 empty] | 112303001105 | [56 empty] | 0.7 | [10 empty] | 0.3 | [11 empty] | 30 | 2 | 23.5 | 820 | 0.8 | 1.4 | 24 | 1125 | 1.6 | 1.4 | 26 | 1400
[28 empty] | 112303701105 | [56 empty] | 0.7 | [10 empty] | 0.3 | [11 empty] | 37 | 2 | 26 | 665 | 0.8 | 1.4 | 26 | 1325 | 1.6 | 1.4 | 28 | 1550
[28 empty] | 112304001105 | [56 empty] | 0.7 | [10 empty] | 0.3 | [11 empty] | 40 | 2 | 26 | 1050 | 0.8 | 1.4 | 26.5 | 1400 | 1.6 | 1.4 | 29.5 | 1700
[28 empty] | 112304401105 | [56 empty] | 0.7 | [10 empty] | 0.3 | [11 empty] | 44 | 2 | 28 | 1150 | 0.8 | 1.4 | 28.5 | 1500 | 1.6 | 1.56 | 30.5 | 1850
[28 empty] | 112305201105 | [56 empty] | 0.7 | [10 empty] | 0.3 | [11 empty] | 52 | 2 | 29 | 1300 | 0.8 | 1.56 | 30.5 | 1700 | 1.6 | 1.56 | 32 | 2050
[28 empty] | 112306101105 | [56 empty] | 0.7 | [10 empty] | 0.4 | [11 empty] | 61 | 2.2 | 31 | 1500 | 0.8 | 1.56 | 32 | 1950 | 2 | 1.56 | 34.5 | 2550
https://www.rrkabel.com/power-cables/power-cables-2xy2xfy2xwy-2-5-sq-mm | 2XY/2XFY/2XWY-2.5 Sq. mm | ['https://www.rrkabel.com/Uploads/Products/125/ProductZoomForMoreDetailsImage/02.jpg', 'https://www.rrkabel.com/Uploads/Products/125/ProductZoomImage/03.jpg', 'https://www.rrkabel.com/Uploads/Products/373/ProductFeaturesDetails/01.png', 'https://www.rrkabel.com/Uploads/Products/373/ProductFeaturesDetails/01.png'] | ['2.5 Sq. mm copper conductor, XLPE insulated unarmoured & galvanised steel strip / wire armoured control cables as per IS 7098 Part - 1.'] | ['CU conductor solid as per Cl. 1 IS 8130 or stranded as per Cl. 2 IS 8130'] | ['Crosslinked polyethylene (XLPE)'] |  | ['PVC Type ST - 2 as per IS 5831 (Option : FR Type / FRLS Type)'] | [9 empty] | ['PVC / PVC tape as per IS 7098 ( P-1 )'] | [8 empty] | ['Single armouring of galvanised steel strip / wire'] | [37 empty] | ['Up to 5 cores by colour coding & more than 5 cores number printing on core as per IS 7098 Part - 1']
[28 empty] | 112400201205 | [56 empty] | 0.7 | [10 empty] | 0.3 | [11 empty] | 2 | 1.8 | 10.5 | 170 |  |  |  |  | 1.4 | 1.24 | 12.5 | 390
[28 empty] | 112400301205 | [56 empty] | 0.7 | [10 empty] | 0.3 | [11 empty] | 3 | 1.8 | 11.5 | 200 |  |  |  |  | 1.4 | 1.24 | 13 | 420
[28 empty] | 112400401205 | [56 empty] | 0.7 | [10 empty] | 0.3 | [11 empty] | 4 | 1.8 | 12 | 235 |  |  |  |  | 1.4 | 1.24 | 14 | 480
[28 empty] | 112400501205 | [56 empty] | 0.7 | [10 empty] | 0.3 | [11 empty] | 5 | 1.8 | 13 | 270 |  |  |  |  | 1.4 | 1.24 | 15 | 540
[28 empty] | 112400601205 | [56 empty] | 0.7 | [10 empty] | 0.3 | [11 empty] | 6 | 1.8 | 14 | 310 |  |  |  |  | 1.4 | 1.24 | 15.5 | 595
[28 empty] | 112400701205 | [56 empty] | 0.7 | [10 empty] | 0.3 | [11 empty] | 7 | 1.8 | 14 | 335 |  |  |  |  | 1.4 | 1.24 | 15.5 | 620
[28 empty] | 112401001205 | [56 empty] | 0.7 | [10 empty] | 0.3 | [11 empty] | 10 | 1.8 | 17 | 350 |  |  |  |  | 1.6 | 1.4 | 19.5 | 870
[28 empty] | 112401201205 | [56 empty] | 0.7 | [10 empty] | 0.3 | [11 empty] | 12 | 1.8 | 19 | 520 | 0.8 | 1.4 | 19 | 760 | 1.6 | 1.4 | 21 | 985
[28 empty] | 112401401205 | [56 empty] | 0.7 | [10 empty] | 0.3 | [11 empty] | 14 | 1.8 | 19.5 | 575 | 0.8 | 1.4 | 19.5 | 820 | 1.6 | 1.4 | 21.5 | 1030
[28 empty] | 112401601205 | [56 empty] | 0.7 | [10 empty] | 0.3 | [11 empty] | 16 | 2 | 20 | 655 | 0.8 | 1.4 | 20 | 890 | 1.6 | 1.4 | 22 | 1105
[28 empty] | 112401901205 | [56 empty] | 0.7 | [10 empty] | 0.3 | [11 empty] | 19 | 2 | 21 | 745 | 0.8 | 1.4 | 21 | 990 | 1.6 | 1.4 | 23 | 1225
[28 empty] | 112402401205 | [56 empty] | 0.7 | [10 empty] | 0.3 | [11 empty] | 24 | 2 | 23.5 | 910 | 0.8 | 1.4 | 24 | 1210 | 1.6 | 1.4 | 25.5 | 1470
[28 empty] | 112402701205 | [56 empty] | 0.7 | [10 empty] | 0.3 | [11 empty] | 27 | 2 | 24 | 1040 | 0.8 | 1.4 | 24.5 | 1300 | 1.6 | 1.4 | 26.5 | 1580
[28 empty] | 112403001205 | [56 empty] | 0.7 | [10 empty] | 0.3 | [11 empty] | 30 | 2 | 25 | 1085 | 0.8 | 1.4 | 25.5 | 1400 | 1.6 | 1.4 | 27 | 1680
[28 empty] | 112403701205 | [56 empty] | 0.7 | [10 empty] | 0.3 | [11 empty] | 37 | 2 | 27 | 1290 | 0.8 | 1.4 | 27.5 | 1635 | 1.6 | 1.56 | 29 | 1950
[28 empty] | 112404001205 | [56 empty] | 0.7 | [10 empty] | 0.3 | [11 empty] | 40 | 2 | 28 | 1390 | 0.8 | 1.56 | 28.5 | 1770 | 1.6 | 1.56 | 30.5 | 2145
[28 empty] | 112404401205 | [56 empty] | 0.7 | [10 empty] | 0.4 | [11 empty] | 44 | 2.2 | 31 | 1550 | 0.8 | 1.56 | 31 | 1950 | 2 | 1.56 | 33.5 | 2525
[28 empty] | 112405201205 | [56 empty] | 0.7 | [10 empty] | 0.4 | [11 empty] | 52 | 2.2 | 32 | 1790 | 0.8 | 1.56 | 32.5 | 2200 | 2 | 1.56 | 35 | 2785
[28 empty] | 112406101205 | [56 empty] | 0.7 | [10 empty] | 0.4 | [11 empty] | 61 | 2.2 | 34 | 2050 | 0.8 | 1.56 | 34 | 2490 | 2 | 1.56 | 36.5 | 3105
https://www.rrkabel.com/power-cables/power-cables-nyy | NYY | ['https://www.rrkabel.com/Uploads/Products/126/ProductZoomForMoreDetailsImage/02.jpg', 'https://www.rrkabel.com/Uploads/Products/126/ProductZoomImage/03.jpg', 'https://www.rrkabel.com/Uploads/Products/376/ProductFeaturesDetails/01.png', 'https://www.rrkabel.com/Uploads/Products/376/ProductFeaturesDetails/01.png'] | ['Plain copper conductor, to DIN VDE 0295.', 'Cl. 1 or Cl. 2 solid or stranded type, BS 6360.', 'Cl. 1 or Cl.2, IEC 60228 and HD 383.', 'PVC core insulation, DIV4 to HD 603.1.', 'Cores stranded concentrically.', 'Colour coded to DIN VDE 0293 - 308, 0276 part 603 or HD 186.', 'Core colour for 3 + 1/2 conductor.'] | [55 empty] | ['Kindly complete the part numbers for these cables by adding the suffix (in place of ‘xx’) for the type required: 01 – J – Type, 02 – O – Type.'] | [60 empty] | ['Power cables for energy supply are installed in open air, in underground, in water, indoors, in cable ducts, power stations, for industry and distribution boards as well as in subscriber networks, where mechanical damages are not to be expected.'] | ['Flexing - 5°C to + 50°C. Fixed installation -20°C to +70°C'] | ['UO / U 0.6 / 1 kV'] | ['4 kV'] | ['50 N/mm²'] | ['gnyl (1/2) bn, bk, gy.'] | ['bu (1/2) bn, bk, gy.', 'PVC outer jacket, DMV5 to HD 603.1.'] | ['Flame propagation test according to IEC 60332 - 1 - 2.Highest permissible voltage.Direct current systems 1.8 kV.Alternating current systems, single-phase systems 1.4 kV. Both conductor insulated, single-phase systems 0.7 kV.One conductor earthed, three-phase systems 1.2 kV with concentric conductor and a cross-section of 240 mm² and above 3.6 kV.']
[128 empty] | 112500101xx11 | 1x 4 re | 6.5 | 34 | 80
[128 empty] | 112500102xx11 | 1x 6 re | 7 | 51 | 102
[128 empty] | 112500103xx11 | 1x 10 re | 7.9 | 86 | 147
[128 empty] | 112500104xx11 | 1x 16 re | 8.9 | 137 | 210
[128 empty] | 112500105xx11 | 1x 25 rm | 11.3 | 217 | 335
[128 empty] | 112500106xx11 | 1x 35 rm | 12.5 | 301 | 439
[128 empty] | 112500107xx11 | 1x 50 rm | 14.3 | 408 | 587
[128 empty] | 112500108xx11 | 1x 70 rm | 16.2 | 589 | 807
[128 empty] | 112500109xx11 | 1x 95 rm | 18.6 | 818 | 1100
[128 empty] | 112500110xx11 | 1x 120 rm | 20.3 | 1031 | 1357
[128 empty] | 112500111xx11 | 1x 150 rm | 22.4 | 1273 | 1665
[128 empty] | 112500112xx11 | 1x 185 rm | 24.8 | 1592 | 2067
[128 empty] | 112500113xx11 | 1x 240 rm | 28 | 2093 | 2686
[128 empty] | 112500114xx11 | 1x 300 rm | 30.9 | 2626 | 3341
[128 empty] | 112500115xx11 | 1x 400 rm | 34.5 | 3357 | 4231
[128 empty] | 112500116xx11 | 1x 500 rm | 38.5 | 4311 | 5379
[128 empty] | 112500117xx11 | 1x 630 rm | 42.7 | 5576 | 6846
[128 empty] | 112500118xx11 | 2x 1.5 re | 10.5 | 26.1 | 156.1
[128 empty] | 112500119xx11 | 2x 2.5 re | 11.3 | 42.6 | 191.5
[128 empty] | 112500120xx11 | 2x 4 re | 13.1 | 68.5 | 268.5
[128 empty] | 112500121xx11 | 2x 6 re | 14.2 | 102.5 | 332.4
[128 empty] | 112500122xx11 | 2x 10 re | 15.9 | 172.5 | 454.4
[128 empty] | 112500123xx11 | 2x 16 re | 17.9 | 274.4 | 621.1
[128 empty] | 112500124xx11 | 2x 25 rm | 24.2 | 441.9 | 1089
[128 empty] | 112500125xx11 | 3x 1.5 re | 11 | 39.1 | 180
[128 empty] | 112500126xx11 | 3x 2.5 re | 11.9 | 63.9 | 225
[128 empty] | 112500127xx11 | 3x 4 re | 13.9 | 102.7 | 320
[128 empty] | 112500128xx11 | 3x 6 re | 15 | 153.7 | 403
[128 empty] | 112500129xx11 | 3x 10 re | 16.9 | 258.7 | 564
[128 empty] | 112500130xx11 | 3x 16 re | 19 | 411.6 | 785
[128 empty] | 112500131xx11 | 3x 25 rm | 24.2 | 662.8 | 1270
[128 empty] | 112500132xx11 | 3x 35 sm | 22.6 | 901.4 | 1382
[128 empty] | 112500133xx11 | 3x 50 sm | 25.7 | 1220.5 | 1829
[128 empty] | 112500134xx11 | 3x 70 sm | 28.7 | 1762.5 | 2487
[128 empty] | 112500135xx11 | 3x 95 sm | 33.3 | 2447.4 | 3410
[128 empty] | 112500136xx11 | 3x 120 sm | 35.9 | 3087.2 | 4171
[128 empty] | 112500137xx11 | 3x 150 sm | 39.5 | 3809.3 | 5107
[128 empty] | 112500138xx11 | 3x 185 sm | 44 | 4766.4 | 6372
[128 empty] | 112500139xx11 | 3x 240 sm | 49.3 | 6264.6 | 8234
[128 empty] | 112500140xx11 | 4x 1.5 re | 11.8 | 52.2 | 214
[128 empty] | 112500141xx11 | 4x 2.5 re | 12.8 | 85.2 | 271
[128 empty] | 112500142xx11 | 4x 4 re | 15 | 136.9 | 390
[128 empty] | 112500143xx11 | 4x 6 re | 16.3 | 204.9 | 496
[128 empty] | 112500144xx11 | 4x 10 re | 18.4 | 344.9 | 701
[128 empty] | 112500145xx11 | 4x 16 re | 20.7 | 548.9 | 986
[128 empty] | 112500146xx11 | 4x 25 rm | 26.7 | 883.7 | 1604
[128 empty] | 112500147xx11 | 4x 35 sm | 27.1 | 1201.9 | 1813
[128 empty] | 112500148xx11 | 4x 50 sm | 30.9 | 1627.4 | 2404
[128 empty] | 112500149xx11 | 4x 70 sm | 35.3 | 2350 | 3324
[128 empty] | 112500150xx11 | 4x 95 sm | 40.5 | 3263.2 | 4512
[128 empty] | 112500151xx11 | 4x 120 sm | 44.3 | 4116.3 | 5582
[128 empty] | 112500152xx11 | 4x 150 sm | 48.8 | 5079 | 6833
[128 empty] | 112500153xx11 | 4x 185 sm | 54.3 | 6355.2 | 8520
[128 empty] | 112500154xx11 | 4x 240 sm | 61 | 8352.7 | 11016
[128 empty] | 112500155xx11 | 5x 1.5 re | 12.7 | 65.2 | 251
[128 empty] | 112500156xx11 | 5x 2.5 re | 13.8 | 106.5 | 321
[128 empty] | 112500157xx11 | 5x 4 re | 16.3 | 171.1 | 467
[128 empty] | 112500158xx11 | 5x 6 re | 17.7 | 256.2 | 597
[128 empty] | 112500159xx11 | 5x 10 re | 20 | 431.1 | 851
[128 empty] | 112500160xx11 | 5x 16 re | 22.7 | 686.1 | 1203
[128 empty] | 112500161xx11 | 5x 25 rm | 29.3 | 1104.6 | 1966
[128 empty] | 112500162xx11 | 5x 35 rm | 32.9 | 1532.6 | 2602
[128 empty] | 112500163xx11 | 5x 50 rm | 37.9 | 2075.1 | 3482
[128 empty] | 112500164xx11 | 7x 1.5 re | 13.6 | 91.3 | 295
[128 empty] | 112500165xx11 | 7x 2.5 re | 14.9 | 149.1 | 384
[128 empty] | 112500166xx11 | 7x 4 re | 17.6 | 239.6 | 564
[128 empty] | 112500167xx11 | 7x 6 re | 19.2 | 358.6 | 731
[128 empty] | 112500168xx11 | 7x 10 re | 21.8 | 603.6 | 1058
[128 empty] | 112500169xx11 | 10 x 1.5 re | 18.5 | 130.4 | 477
[128 empty] | 112500170xx11 | 10 x 2.5 re | 18.4 | 213 | 543
[128 empty] | 112500171xx11 | 12 x 1.5 re | 17.3 | 156.5 | 466
[128 empty] | 112500172xx11 | 12 x 2.5 re | 19 | 255.5 | 616
[128 empty] | 112500173xx11 | 14 x 1.5 re | 18.1 | 182.6 | 524
[128 empty] | 112500174xx11 | 14 x 2.5 re | 19.9 | 298.1 | 696
[128 empty] | 112500175xx11 | 16 x 1.5 re | 19 | 208.7 | 584
[128 empty] | 112500176xx11 | 16 x 2.5 re | 20.9 | 340.7 | 779
[128 empty] | 112500177xx11 | 19 x 1.5 re | 20 | 247.8 | 667
[128 empty] | 112500178xx11 | 19 x 2.5 re | 22 | 404.6 | 895
[128 empty] | 112500179xx11 | 21 x 1.5 re | 21 | 273.9 | 731
[128 empty] | 112500180xx11 | 21 x 2.5 re | 23.2 | 447.2 | 983
[128 empty] | 112500181xx11 | 24 x 1.5 re | 23.1 | 273.9 | 779
[128 empty] | 112500182xx11 | 24 x 2.5 re | 25.6 | 511.1 | 1133
[128 empty] | 112500183xx11 | 30 x 1.5 re | 24.4 | 391.2 | 999
[128 empty] | 112500184xx11 | 30 x 2.5 re | 27 | 638.9 | 1354
[128 empty] | 112500185xx11 | 40 x 1.5 re | 27.4 | 521.6 | 1282
[128 empty] | 112500186xx11 | 40 x 2.5 re | 30.8 | 851.8 | 1782
[128 empty] | 112500187xx11 | 52 x 2.5 re | 34.6 | 1107.4 | 2268
[128 empty] | 112500188xx11 | 61 x 1.5 re | 33.1 | 795.5 | 1905
[128 empty] | 112500189xx11 | 3×25/16rm | 23.6 | 786.6 | 200
[128 empty] | 112500190xx11 | 3×25/1sm | 23.6 | 1038.3 | 225
[128 empty] | 112500190xx11 | 3×35/16sm | 25.4 | 1437.1 | 281
[128 empty] | 112500191xx11 | 3×50/25sm | 29.3 | 2063 | 346
[128 empty] | 112500192xx11 | 3×70/35sm | 33.3 | 2854.2 | 433
[128 empty] | 112500193xx11 | 3×95/50sm | 38.1 | 3674.7 | 503
[128 empty] | 112500194xx11 | 3×120/70sm | 41.7 | 4396.8 | 580
[128 empty] | 112500195xx11 | 3×150/70sm | 45.4 | 5582.2 | 698
[128 empty] | 112500196xx11 | 3×185/95sm | 50.6 | 7293.6 | 854
[128 empty] | 112500197xx11 | 3×240/120sm | 56.8 | 9129.1 | 1013
[128 empty] | 112500198xx11 | 3×300/150sm | 62.7
https://www.rrkabel.com/power-cables/power-cables-bs-5467 | POWER CABLE-BS 5467 | ['https://www.rrkabel.com/Uploads/Products/127/ProductZoomForMoreDetailsImage/02.jpg', 'https://www.rrkabel.com/Uploads/Products/127/ProductZoomImage/03.jpg', 'https://www.rrkabel.com/Uploads/Products/379/ProductFeaturesDetails/01.png', 'https://www.rrkabel.com/Uploads/Products/379/ProductFeaturesDetails/01.png'] | ['Single, two, three, four and five core cables. Stranded plain copper conductors, XLPE insulated, cores laid up, extruded PVC bedding,', 'galvanised steel wire armoured (Aluminium wires for single cores) and PVC sheathed.'] | [116 empty] | ['Industrial wiring and mains distribution. Can be laid direct in the ground, or in ducts, clipped to surface, on trays or in free air. May be embedded in concrete.'] | [12 empty] | ['BS 5467'] | ['600/1000V'] | ['15 x Cable diameter'] | ['Single core : Brown or blue.', 'Two core : Brown, blue.', 'Three core : Brown, black, grey.', 'Four core : Brown, black, grey, blue.', 'Five code : Brown, black, grey, green/yellow, blue.', '(There is the option for core colour as per customer requirement).'] | ['Where a conductor operates at a temperature exceeding 70°C it shall be ascertained that the equipment connected to the conductor is suitable for the conductor operating temperature (see regulation 512-1-2 of BS 7671, the 17th Edition of IEE Wiring Regulations).', 'Cables with reduced Flame Propagation and designs with alternative core identification are available to order.']
[8 empty] | 112600100050 | 50 | [128 empty] | Single Core Aluminium Wire Armour | 1 | 0.9 | 12.7 | 17.5 | 800 | 0.387 | 0.4938 | 0.104 | 0.505 | 0.41 | 1.3
[8 empty] | 112600100070 | 70 | [128 empty] | Single Core Aluminium Wire Armour | 1.1 | 1.25 | 14.7 | 20.2 | 960 | 0.268 | 0.341 | 0.101 | 0.356 | 0.46 | 0.75
[8 empty] | 112600100095 | 95 | [128 empty] | Single Core Aluminium Wire Armour | 1.1 | 1.25 | 16.6 | 22.3 | 1240 | 0.193 | 0.2469 | 0.097 | 0.265 | 0.53 | 0.67
[8 empty] | 112600100120 | 120 | [128 empty] | Single Core Aluminium Wire Armour | 1.2 | 1.25 | 18.5 | 24.2 | 1510 | 0.153 | 0.1962 | 0.094 | 0.217 | 0.56 | 0.61
[8 empty] | 112600100150 | 150 | [128 empty] | Single Core Aluminium Wire Armour | 1.4 | 1.6 | 20.8 | 27.4 | 1900 | 0.124 | 0.1594 | 0.095 | 0.186 | 0.52 | 0.42
[8 empty] | 112600100185 | 185 | [128 empty] | Single Core Aluminium Wire Armour | 1.6 | 1.6 | 23.2 | 30 | 2320 | 0.0991 | 0.128 | 0.093 | 0.158 | 0.54 | 0.38
[8 empty] | 112600100240 | 240 | [128 empty] | Single Core Aluminium Wire Armour | 1.7 | 1.6 | 26 | 32.8 | 2930 | 0.0754 | 0.0985 | 0.09 | 0.134 | 0.59 | 0.34
[8 empty] | 112600100300 | 300 | [128 empty] | Single Core Aluminium Wire Armour | 1.8 | 1.6 | 28.6 | 35.6 | 3580 | 0.0601 | 0.0797 | 0.088 | 0.119 | 0.63 | 0.31
[8 empty] | 112600100400 | 400 | [128 empty] | Single Core Aluminium Wire Armour | 2 | 2 | 32.4 | 40.4 | 4600 | 0.047 | 0.0635 | 0.089 | 0.109 | 0.62 | 0.22
[8 empty] | 112600100500 | 500 | [128 empty] | Single Core Aluminium Wire Armour | 2.2 | 2 | 36 | 44.2 | 5770 | 0.0366 | 0.0513 | 0.087 | 0.101 | 0.66 | 0.2
[8 empty] | 112600100630 | 630 | [128 empty] | Single Core Aluminium Wire Armour | 2.4 | 2 | 40.4 | 48.8 | 7250 | 0.0283 | 0.0419 | 0.085 | 0.095 | 0.7 | 0.18
[8 empty] | 112600100800 | 800 | [128 empty] | Single Core Aluminium Wire Armour | 2.6 | 2.5 | 45.6 | 55.4 | 9381 | 0.0221 | 0.0349 | 0.087 | 0.094 | 0.85 | 0.13
[8 empty] | 112600101000 | 1000 | [128 empty] | Single Core Aluminium Wire Armour | 2.8 | 2.5 | 50.6 | 60.6 | 11540 | 0.0176 | 0.0303 | 0.085 | 0.09 | 0.87 | 0.12
[8 empty] | 112600201105 | 1.5 | [128 empty] | Two Core Steel Wire Armour | 0.6 | 0.9 | 7.3 | 12.1 | 302 | 12.1 | 15.428 | 0.104 | 15.428 | 0.23 | 10.2
[8 empty] | 112600201205 | 2.5 | [128 empty] | Two Core Steel Wire Armour | 0.7 | 0.9 | 8.5 | 13.6 | 346 | 7.41 | 9.448 | 0.101 | 9.449 | 0.25 | 8.8
[8 empty] | 112600200004 | 4 | [128 empty] | Two Core Steel Wire Armour | 0.7 | 0.9 | 9.4 | 14.7 | 410 | 4.61 | 5.878 | 0.099 | 5.879 | 0.27 | 7.9
[8 empty] | 112600200006 | 6 | [128 empty] | Two Core Steel Wire Armour | 0.7 | 0.9 | 10.5 | 15.9 | 499 | 3.08 | 3.927 | 0.094 | 3.928 | 0.3 | 7
[8 empty] | 112600200010 | 10 | [128 empty] | Two Core Steel Wire Armour | 0.7 | 0.9 | 12.3 | 18 | 648 | 1.83 | 2.333 | 0.093 | 2.335 | 0.32 | 6
[8 empty] | 112600200016 | 16 | [128 empty] | Two Core Steel Wire Armour | 0.7 | 1.25 | 14.3 | 20.4 | 978 | 1.15 | 1.466 | 0.088 | 1.469 | 0.35 | 3.7
[8 empty] | 112600200025 | 25 | [128 empty] | Two Core Steel Wire Armour | 0.9 | 1.25 | 14.7 | 20.4 | 1290 | 0.727 | 0.926 | 0.082 | 0.93 | 0.38 | 3.7
[8 empty] | 112600200035 | 35 | [128 empty] | Two Core Steel Wire Armour | 0.9 | 1.6 | 16.8 | 23.3 | 1500 | 0.524 | 0.6685 | 0.077 | 0.673 | 0.42 | 2.6
[8 empty] | 112600200050 | 50 | [128 empty] | Two Core Steel Wire Armour | 1 | 1.6 | 19 | 25.8 | 1890 | 0.387 | 0.494 | 0.076 | 0.5 | 0.45 | 2.3
[8 empty] | 112600200070 | 70 | [128 empty] | Two Core Steel Wire Armour | 1.1 | 1.6 | 22 | 29 | 2450 | 0.268 | 0.3412 | 0.075 | 0.349 | 0.49 | 2
[8 empty] | 112600200095 | 95 | [128 empty] | Two Core Steel Wire Armour | 1.1 | 2 | 25.1 | 33.1 | 3300 | 0.193 | 0.2471 | 0.074 | 0.258 | 0.55 | 1.4
[8 empty] | 112600200120 | 120 | [128 empty] | Two Core Steel Wire Armour | 1.2 | 2 | 27.9 | 36.1 | 4020 | 0.153 | 0.1964 | 0.072 | 0.209 | 0.57 | 1.3
[8 empty] | 112600200150 | 150 | [128 empty] | Two Core Steel Wire Armour | 1.4 | 2 | 30.9 | 39.3 | 4750 | 0.124 | 0.1597 | 0.073 | 0.176 | 0.57 | 120
[8 empty] | 112600200185 | 185 | [128 empty] | Two Core Steel Wire Armour | 1.6 | 2.5 | 34.9 | 44.7 | 6180 | 0.0991 | 0.1284 | 0.073 | 0.148 | 0.55 | 0.82
[8 empty] | 112600200240 | 240 | [128 empty] | Two Core Steel Wire Armour | 1.7 | 2.5 | 39 | 49 | 7570 | 0.0754 | 0.0989 | 0.072 | 0.122 | 0.6 | 0.73
[8 empty] | 112600200300 | 300 | [128 empty] | Two Core Steel Wire Armour | 1.8 | 2.5 | 43.3 | 53.5 | 9180 | 0.0601 | 0.0801 | 0.072 | 0.107 | 0.62 | 0.67
[8 empty] | 112600200400 | 400 | [128 empty] | Two Core Steel Wire Armour | 2 | 2.5 | 48.4 | 59 | 10500 | 0.047 | 0.0641 | 0.071 | 0.096 | 0.64 | 0.59
[8 empty] | 112600301105 | 1.5 | [128 empty] | Three Core Steel Wire Armour | 0.6 | 0.9 | 7.8 | 12.6 | 330 | 12.1 | 15.428 | 0.104 | 15.428 | 0.23 | 9.5
[8 empty] | 112600301205 | 2.5 | [128 empty] | Three Core Steel Wire Armour | 0.7 | 0.9 | 9.2 | 14.1 | 390 | 7.41 | 9.448 | 0.101 | 9.449 | 0.25 | 8.2
[8 empty] | 112600300004 | 4 | [128 empty] | Three Core Steel Wire Armour | 0.7 | 0.9 | 10 | 15.3 | 464 | 4.61 | 5.878 | 0.099 | 5.879 | 0.27 | 7.5
[8 empty] | 112600300006 | 6 | [128 empty] | Three Core Steel Wire Armour | 0.7 | 0.9 | 11.2 | 16.6 | 568 | 3.08 | 3.927 | 0.094 | 3.928 | 0.3 | 6.7
[8 empty] | 112600300010 | 10 | [128 empty] | Three Core Steel Wire Armour | 0.7 | 1.25 | 13.1 | 19.5 | 866 | 1.83 | 2.333 | 0.093 | 2.335 | 0.32 | 4
[8 empty] | 112600300016 | 16 | [128 empty] | Three Core Steel Wire Armour | 0.7 | 1.25 | 15.3 | 21.6 | 1152 | 1.15 | 1.466 | 0.088 | 1.469 | 0.35 | 3.5
[8 empty] | 112600300025 | 25 | [128 empty] | Three Core Steel Wire Armour | 0.9 | 1.6 | 18.9 | 25.5 | 1800 | 0.727 | 0.926 | 0.082 | 0.93 | 0.37 | 2.5
[8 empty] | 112600300035 | 35 | [128 empty] | Three Core Steel Wire Armour | 0.9 | 1.6 | 21.3 | 28 | 2230 | 0.524 | 0.6685 | 0.077 | 0.673 | 0.42 | 2.3
[8 empty] | 112600300050 | 50 | [128 empty] | Three Core Steel Wire Armour | 1 | 1.6 | 21.7 | 28.5 | 2490 | 0.387 | 0.494 | 0.076 | 0.5 | 0.45 | 2
[8 empty] | 112600300070 | 70 | [128 empty] | Three Core Steel Wire Armour | 1.1 | 1.6 | 25.2 | 32.2 | 3290 | 0.268 | 0.3412 | 0.075 | 0.349 | 0.49 | 1.8
[8 empty] | 112600300095 | 95 | [128 empty] | Three Core Steel Wire Armour | 1.1 | 2 | 28.8 | 37 | 4440 | 0.193 | 0.2471 | 0.074 | 0.258 | 0.55 | 1.3
[8 empty] | 112600300120 | 120 | [128 empty] | Three Core Steel Wire Armour | 1.2 | 2 | 32 | 40.4 | 5470 | 0.153 | 0.1964 | 0.072 | 0.209 | 0.57 | 1.2
[8 empty] | 112600300150 | 150 | [128 empty] | Three Core Steel Wire Armour | 1.4 | 2.5 | 35.9 | 45.5 | 6930 | 0.124 | 0.1597 | 0.073 | 0.176 | 0.55 | 0.78
[8 empty] | 112600300185 | 185 | [128 empty] | Three Core Steel Wire Armour | 1.6 | 2.5 | 40 | 49.8 | 8350 | 0.0991 | 0.1284 | 0.073 | 0.148 | 0.55 | 0.71
[8 empty] | 112600300240 | 240 | [128 empty] | Three Core Steel Wire Armour | 1.7 | 2.5 | 44.9 | 55.1 | 10400 | 0.0754 | 0.0989 | 0.072 | 0.122 | 0.6 | 0.63
[8 empty] | 112600300300 | 300 | [128 empty] | Three Core Steel Wire Armour | 1.8 | 2.5 | 49.8 | 60.2 | 12600 | 0.0601 | 0.0801 | 0.072 | 0.107 | 0.62 | 0.58
[8 empty] | 112600300400 | 400 | [128 empty] | Three Core Steel Wire Armour | 2 | 2.5 | 55.8 | 66.6 | 14600 | 0.047 | 0.0641 | 0.071 | 0.096 | 0.64 | 0.52
[8 empty] | 112600401105 | 1.5 | [128 empty] | Four Core Steel Wire Armour | 0.6 | 0.9 | 8.5 | 13.5 | 365 | 12.1 | 15.428 | 0.104 | 15.428 | 0.23 | 8.8
[8 empty] | 112600401205 | 2.5 | [128 empty] | Four Core Steel Wire Armour | 0.7 | 0.9 | 9.9 | 15 | 438 | 7.41 | 9.448 | 0.101 | 9.449 | 0.25 | 7.7
[8 empty] | 112600400004 | 4 | [128 empty] | Four Core Steel Wire Armour | 0.7 | 0.9 | 11 | 16.4 | 532 | 4.61 | 5.878 | 0.099 | 5.879 | 0.27 | 6.8
[8 empty] | 112600400006 | 6 | [128 empty] | Four Core Steel Wire Armour | 0.7 | 1.25 | 12.3 | 18.7 | 764 | 3.08 | 3.927 | 0.094 | 3.928 | 0.3 | 4.3
[8 empty] | 112600400010 | 10 | [128 empty] | Four Core Steel Wire Armour | 0.7 | 1.25 | 14.5 | 21.1 | 1013 | 1.83 | 2.333 | 0.093 | 2.336 | 0.32 | 3.7
[8 empty] | 112600400016 | 16 | [128 empty] | Four Core Steel Wire Armour | 0.7 | 1.25 | 17 | 22.9 | 1360 | 1.15 | 1.466 | 0.088 | 1.469 | 0.35 | 3.1
[8 empty] | 112600400025 | 25 | [128 empty] | Five Core Steel Wire Armour | 0.9 | 1.6 | 21 | 27.6 | 2160 | 0.727 | 0.926 | 0.082 | 0.93 | 0.37 | 2.3
[8 empty] | 112600400035 | 35 | [128 empty] | Five Core Steel Wire Armour | 0.9 | 1.6 | 23.6 | 30.4 | 2690 | 0.524 | 0.6685 | 0.077 | 0.673 | 0.42 | 2
[8 empty] | 112600400050 | 50 | [128 empty] | Five Core Steel Wire Armour | 1 | 1.6 | 25 | 32 | 3130 | 0.387 | 0.494 | 0.076 | 0.5 | 0.45 | 1.8
[8 empty] | 112600400070 | 70 | [128 empty] | Five Core Steel Wire Armour | 1.1 | 2 | 29.5 | 37.7 | 4500 | 0.268 | 0.3412 | 0.075 | 0.349 | 0.48 | 1.2
[8 empty] | 112600400095 | 95 | [128 empty] | Five Core Steel Wire Armour | 1.1 | 2 | 33.3 | 41.7 | 5600 | 0.193 | 0.2471 | 0.074 | 0.258 | 0.55 | 1.1
[8 empty] | 112600400120 | 120 | [128 empty] | Five Core Steel Wire Armour | 1.2 | 2.5 | 37.5 | 47.1 | 7400 | 0.153 | 0.1964 | 0.072 | 0.209 | 0.55 | 0.76
[8 empty] | 112600400150 | 150 | [128 empty] | Five Core Steel Wire Armour | 1.4 | 2.5 | 41.6 | 51.4 | 8780 | 0.124 | 0.1597 | 0.073 | 0.176 | 0.55 | 0.68
[8 empty] | 112600400185 | 185 | [128 empty] | Five Core Steel Wire Armour | 1.6 | 2.5 | 46.4 | 56.6 | 10630 | 0.0991 | 0.1284 | 0.073 | 0.148 | 0.55 | 0.61
[8 empty] | 112600400240 | 240 | [128 empty] | Five Core Steel Wire Armour | 1.7 | 2.5 | 52.6 | 63 | 13390 | 0.0754 | 0.0989 | 0.072 | 0.122 | 0.58 | 0.54
[8 empty] | 112600400300 | 300 | [128 empty] | Five Core Steel Wire Armour | 1.8 | 2.5 | 58 | 68.8 | 16290 | 0.0601 | 0.0801 | 0.072 | 0.107 | 0.62 | 0.49
[8 empty] | 112600400400 | 400 | [128 empty] | Five Core Steel Wire Armour | 2 | 3.15 | 65.4 | 78.1 | 19800 | 0.047 | 0.0641 | 0.071 | 0.096 | 0.63 | 0.35
[8 empty] | 112600501105 | 1.5 | [128 empty] | Five Core Steel Wire Armour | 0.6 | 0.9 | 9.7 | 14.3 | 410 | 12.1 | 15.428 | 0.104 | 15.428 | 0.23 | 8.2
[8 empty] | 112600501205 | 2.5 | [128 empty] | Five Core Steel Wire Armour | 0.7 | 0.9 | 11.7 | 16.3 | 470 | 7.41 | 9.448 | 0.101 | 9.449 | 0.25 | 6.8
[8 empty] | 112600500004 | 4 | [128 empty] | Five Core Steel Wire Armour | 0.7 | 0.9 | 13 | 17.8 | 710 | 4.61 | 5.878 | 0.099 | 5.879 | 0.27 | 6.2
[8 empty] | 112600500006 | 6 | [128 empty] | Five Core Steel Wire Armour | 0.7 | 1.25 | 14.5 | 20 | 876 | 3.08 | 3.927 | 0.094 | 3.928 | 0.3 | 3.9
[8 empty] | 112600500010 | 10 | [128 empty] | Five Core Steel Wire Armour | 0.7 | 1.25 | 17.2 | 22.9 | 1165 | 1.83 | 2.333 | 0.093 | 2.336 | 0.32 | 3.4
[8 empty] | 112600500016 | 16 | [128 empty] | Five Core Steel Wire Armour | 0.7 | 1.6 | 20 | 26.6 | 1742 | 1.15 | 1.466 | 0.088 | 1.469 | 0.35 | 2.2
[8 empty] | 112600500025 | 25 | [128 empty] | Five Core Steel Wire Armour | 0.9 | 1.6 | 24.7 | 31.5 | 2323 | 0.727 | 0.926 | 0.082 | 0.93 | 0.37 | 1.8
[8 empty] | 112600500035 | 35 | [128 empty] | Five Core Steel Wire Armour | 0.9 | 1.6 | 27.8 | 34.8 | 2932 | 0.524 | 0.6685 | 0.077 | 0.673 | 0.42 | 1.6
[8 empty] | 112600500050 | 50 | [128 empty] | Five Core Steel Wire Armour | 1 | 2 | 32.4 | 40.4 | 4192 | 0.387 | 0.494 | 0.076 | 0.5 | 0.45 | 1.1
[8 empty] | 112600500070 | 70 | [128 empty] | Five Core Steel Wire Armour | 1.1 | 2 | 37.9 | 46.3 | 5336 | 0.268 | 0.3412 | 0.075 | 0.349 | 0.48 | 0.9
https://www.rrkabel.com/power-cables/exvb | EXVB | ['https://www.rrkabel.com/Uploads/Products/178/ProductZoomForMoreDetailsImage/EXVB216x252.jpg', 'https://www.rrkabel.com/Uploads/Products/178/ProductZoomImage/EXVBwithname.jpg', 'https://www.rrkabel.com/Uploads/Products/495/ProductFeaturesDetails/EXVB_20220404.png', 'https://www.rrkabel.com/Uploads/Products/495/ProductFeaturesDetails/EXVB_20220404.png'] | [117 empty] | ['EXVB is a power distribution cable suitable for low voltage applications in power plants, transformer stations, industrial plants, metropolitan networks and in other electric plants where heavier current and thermal loads are expected.This cable is mainly suitable for fixed installations in ground, canals, concrete and in areas free from heavy mechanical stress.'] | ['-5°C to 90°C'] | ['U', 'O', '/ U 0.6/1.0 kV'] | [10 empty] | ['HD 603 Part 5/ Sect.A & IEC 60502-1'] | [16 empty] | ['Plain Copper conductor RE,RM,SM (Class-1 & Class-2)'] | ['Crosslinked polyethylene (XLPE)'] | [] | ['brown, black & grey'] | ['blue, brown, black, grey'] | ['Special Bedding Compound'] | ['Special PVC outer sheath'] | ['*Water proof variant of this cable, EXeVB is also available with special water blocking tape.']
[77 empty] | 112701010091 | [80 empty] | 3 x 1.5 | 0.7 | 1 | 1.8 | 12 | 209
[77 empty] | 112701020091 | [80 empty] | 3 x 1.5 | 0.7 | 1 | 1.8 | 12 | 199
[77 empty] | 112701030091 | [80 empty] | 3 x 2.5 | 0.7 | 1 | 1.8 | 13 | 257
[77 empty] | 112701040091 | [80 empty] | 3 x 2.5 | 0.7 | 1 | 1.8 | 12 | 244
[77 empty] | 112701050091 | [80 empty] | 3 x 4 | 0.7 | 1 | 1.8 | 14 | 326
[77 empty] | 112701060091 | [80 empty] | 3 x 4 | 0.7 | 1 | 1.8 | 13 | 307
[77 empty] | 112701070091 | [80 empty] | 3 x 6 | 0.7 | 1 | 1.8 | 14 | 385
[77 empty] | 112701080091 | [80 empty] | 3 x 10 | 0.7 | 1 | 1.8 | 16 | 533
[77 empty] | 112701090091 | [80 empty] | 3 x 10 | 0.7 | 1 | 1.8 | 16 | 531
[77 empty] | 112701100091 | [80 empty] | 4 x 1.5 | 0.7 | 1 | 1.8 | 13 | 241
[77 empty] | 112701110091 | [80 empty] | 4 x 1.5 | 0.7 | 1 | 1.8 | 12 | 229
[77 empty] | 112701120091 | [80 empty] | 4 x 2.5 | 0.7 | 1 | 1.8 | 14 | 301
[77 empty] | 112701130091 | [80 empty] | 4 x 2.5 | 0.7 | 1 | 1.8 | 13 | 285
[77 empty] | 112701140091 | [80 empty] | 4 x 4 | 0.7 | 1 | 1.8 | 14 | 365
[77 empty] | 112701150091 | [80 empty] | 4 x 6 | 0.7 | 1 | 1.8 | 16 | 492
[77 empty] | 112701160091 | [80 empty] | 4 x 6 | 0.7 | 1 | 1.8 | 15 | 463
[77 empty] | 112701170091 | [80 empty] | 4 x 10 | 0.7 | 1 | 1.8 | 18 | 679
[77 empty] | 112701180091 | [80 empty] | 4 x 10 | 0.7 | 1 | 1.8 | 17 | 648
[77 empty] | 112701190091 | [80 empty] | 4 x 16 | 0.7 | 1 | 1.8 | 20 | 855
[77 empty] | 112701200091 | [80 empty] | 4 x 25 | 0.9 | 1 | 1.8 | 23 | 1265
[77 empty] | 112701210091 | [80 empty] | 4 x 35 | 0.9 | 1 | 1.8 | 26 | 1653
[77 empty] | 112701220091 | [80 empty] | 4 x 50 | 1 | 1 | 1.87 | 29 | 2168
[77 empty] | 112701230091 | [80 empty] | 4 x 70 | 1.1 | 1.2 | 2.03 | 34 | 3066
[77 empty] | 112701240091 | [80 empty] | 4 x 95 | 1.1 | 1.2 | 2.17 | 38 | 4111
[77 empty] | 112701250091 | [80 empty] | 4 x 120 | 1.2 | 1.2 | 2.3 | 42 | 5109
[77 empty] | 112701260091 | [80 empty] | 4 x 240 | 1.7 | 1.6 | 2.84 | 58 | 10193
[19 empty] | 1.5 | [144 empty] | 28 | 24
[19 empty] | 2.5 | [144 empty] | 35 | 33
[19 empty] | 4 | [144 empty] | 44 | 39
[19 empty] | 6 | [144 empty] | 55 | 50
[19 empty] | 10 | [144 empty] | 74 | 67
[19 empty] | 16 | [144 empty] | 94 | 85
[19 empty] | 95 | [144 empty] | 120 | 125
[19 empty] | 120 | [144 empty] | 145 | 155
[19 empty] | 150 | [144 empty] | 170 | 190
[19 empty] | 185 | [144 empty] | 210 | 235
[19 empty] | 240 | [144 empty] | 250 | 290
https://www.rrkabel.com/power-cables/eaxvb | EAXVB | ['https://www.rrkabel.com/Uploads/Products/179/ProductZoomForMoreDetailsImage/EAXVB216x252.jpg', 'https://www.rrkabel.com/Uploads/Products/179/ProductZoomImage/EAXVBwithname.jpg', 'https://www.rrkabel.com/Uploads/Products/496/ProductFeaturesDetails/EAXeVB_20220404.png', 'https://www.rrkabel.com/Uploads/Products/496/ProductFeaturesDetails/EAXeVB_20220404.png'] | [117 empty] | ['EAXVB is a power distribution cable with aluminium conductor suitable for low voltage applications in power plants, transformer stations, industrial plants, metropolitan networks and in other electric plants where heavier current and thermal loads are expected.This cable is mainly suitable for fixed installations in ground, canals, concrete and in areas free from heavy mechanical stress.'] |  | ['U', 'O', '/ U 0.6/1.0 kV'] | [10 empty] | ['HD 603 Part 5/ Sect.A & IEC 60502-1'] | [16 empty] | ['Aluminium conductor SM (Class-2)'] | ['Crosslinked polyethylene (XLPE)'] | ['blue, brown, black, grey'] |  |  | ['Special Bedding Compound'] | ['Special PVC outer sheath'] | ['*Water proof variant of this cable, EAXeVB is also available with special water blocking tape.'] | [8 empty] | ['-5°C to 90°C']
[77 empty] | 112801010091 | [80 empty] | 4 x 25 | 0.9 | 1 | 1.8 | 24 | 695
[77 empty] | 112801020091 | [80 empty] | 4 x 35 | 0.9 | 1 | 1.8 | 26 | 852
[77 empty] | 112801030091 | [80 empty] | 4 x 50 | 1 | 1 | 1.9 | 29 | 1076
[77 empty] | 112801040091 | [80 empty] | 4 x 70 | 1 | 1.2 | 2 | 34 | 1454
[77 empty] | 112801050091 | [80 empty] | 4 x 95 | 1.1 | 1.2 | 2.2 | 38 | 1892
[77 empty] | 112801060091 | [80 empty] | 4 x 120 | 1.2 | 1.4 | 2.3 | 43 | 2359
[77 empty] | 112801070091 | [80 empty] | 4 x 150 | 1.4 | 1.4 | 2.5 | 47 | 2844
[77 empty] | 112801080091 | [80 empty] | 4 x 185 | 1.6 | 1.4 | 2.6 | 52 | 3488
[77 empty] | 112801090091 | [80 empty] | 4 x 240 | 1.7 | 1.6 | 2.9 | 59 | 4457
[19 empty] | 25 | [144 empty] | 95 | 99
[19 empty] | 35 | [144 empty] | 116 | 117
[19 empty] | 50 | [144 empty] | 140 | 140
[19 empty] | 70 | [144 empty] | 170 | 176
[19 empty] | 95 | [144 empty] | 200 | 221
[19 empty] | 120 | [144 empty] | 225 | 258
[19 empty] | 150 | [144 empty] | 255 | 294
[19 empty] | 185 | [144 empty] | 285 | 339
[19 empty] | 240 | [144 empty] | 325 | 402