## Sheet1
Link | Title | Images | Application | Approvals | Conductor | Voltage | Product Type | Size Range | Specifications | Part Number | Nominal Cross Sectional Area (Sq. mm) | No of Strands/Max. Strand Diameter (mm) | Nominal Insulation Thickness (mm) | Maximum Diameter Over Insulation (mm) | Standard | Voltage Rating | Temperature Range | Minimum Bending Radius | Construction | Properties | ('Part Number', 'Part Number') | ('Part Number', 'Part Number.1') | ('Part Number', 'Part Number.2') | ('Nominal CrossSectional Area (Sq. mm)', 'Nominal CrossSectional Area (Sq. mm)') | ('Nominal CrossSectional Area (Sq. mm)', 'Nominal CrossSectional Area (Sq. mm).1') | ('Nominal Thickness of Insulation (mm)', 'Nominal Thickness of Insulation (mm)') | ('Nominal Thickness of Insulation (mm)', 'Nominal Thickness of Insulation (mm).1') | ('Mean Overall Diameter', 'Lower Limit (mm)') | ('Mean Overall Diameter', 'Lower Limit (mm).1') | ('Mean Overall Diameter', 'Upper Limit (mm)') | ('Mean Overall Diameter', 'Upper Limit (mm).1') | ('Approx. Cable Weight (kg/km)', 'Approx. Cable Weight (kg/km)') | ('Approx. Cable Weight (kg/km)', 'Approx. Cable Weight (kg/km).1') | Nominal Voltage | Harmonised Designation | Cable Construction | Tests | ('Nominal Cross Sectional Area (Sq. mm)', 'Nominal Cross Sectional Area (Sq. mm)') | ('Nominal Cross Sectional Area (Sq. mm)', 'Nominal Cross Sectional Area (Sq. mm).1') | Cable diameter ≤ 8 mm: | Temperature Rating
https://www.rrkabel.com/single-core/ratnaflex-flexible-694 | RATNAFLEX FLEXIBLE | ['https://www.rrkabel.com/Uploads/Products/21/ProductZoomForMoreDetailsImage/02.jpg', 'https://www.rrkabel.com/Uploads/Products/21/ProductZoomImage/03.jpg', 'https://www.rrkabel.com/Uploads/Products/61/ProductFeaturesDetails/01.png', 'https://www.rrkabel.com/Uploads/Products/61/ProductFeaturesDetails/01.png'] | ['Cable designed for internal wiring in switch control, relay and instrumentation panels of power switchgear and for purposes such as stationary, static appliances, internal connectors in rectifier equipment, motor starters and controllers.PVC 70°C cables suitable for general wiring in control cabinets, panels and power switchgear.FR PVC 70°C cables suitable for ambient wiring in control cabinets, panels and power switchgear for enhanced safety. HR PVC 85°C cables suitable for higher ambient wiring in control cabinets, panels and power switchgear.HR FR PVC 85°C cables suitable for higher ambient wiring in control cabinets, panels and power switchgear and enhanced safety.FR-LSH PVC 70°C cables are suitable for wiring in public places like schools, hospitals, theatres, etc. These are also suitable for fire prone areas in industries and commercial infrastructure.'] | ['IS 694 marked, FIA / TAC'] | ['Electrolytic grade annealed copper'] | ['Up to and including 1100V']
[7 empty] | RR KABEL | 0.5 & 0.75 Sq. mm | IS 694, IS 8130 Class 5, IS 5831 Type D
[7 empty] | RATNAFLEX | 1 to 4 | IS 694, IS 8130 Class 5, IS 5831 Type D
[7 empty] | RR KABEL FR | 0.5 to 300 Sq. mm | IS 694, IS 8130 Class 5, IS 5831 Type D (FR)
[7 empty] | RR KABEL FR-LSH | 0.5 to 150 Sq. mm | IS 694, IS 8130 Class 5, IS 5831 Type D (FR-LSH)
[7 empty] | RR KABEL HR | 0.5 & 0.75 Sq. mm, 6 to 16 Sq. mm | IS 694, IS 8130 Class 5, IS 5831 Type C (HR)
[7 empty] | RATNAFLEX HR | 1 to 4 & 25 to 300 Sq. mm | IS 694, IS 8130 Class 5, IS 5831 Type C (HR)
[7 empty] | RR KABEL HR FR | 0.5 to 300 Sq. mm | IS 694, IS 8130 Class 5, IS 5831 Type C (HR FR)
[10 empty] | 02010101xxy0 | 0.5 | 16/0.2 | 0.6 | 2.6
[10 empty] | 02010102xxy0 | 0.75 | 24/0.2 | 0.6 | 2.8
[10 empty] | 02010103xxy0 | 1 | 32/0.2 | 0.6 | 3
[10 empty] | 02010104xxy0 | 1.5 | 30/0.25 | 0.6 | 3.4
[10 empty] | 02010105xxy0 | 2.5 | 50/0.25 | 0.7 | 4.1
[10 empty] | 02010106xxy0 | 4 | 56/0.3 | 0.8 | 4.8
[10 empty] | 02010107xxy0 | 6 | 84/0.3 | 0.8 | 5.3
[10 empty] | 02010108xxy0 | 10 | 140/0.3 | 1 | 7
[10 empty] | 02010109xxy0 | 16 | 126/0.4 | 1 | 8.1
[10 empty] | 02010110xxy0 | 25 | 196/0.4 | 1.2 | 10.2
[10 empty] | 02010111xxy0 | 35 | 276/0.4 | 1.2 | 11.7
[10 empty] | 02010112xxy0 | 50 | 396/0.4 | 1.4 | 13.9
[10 empty] | 02010113xxy0 | 70 | 360/0.5 | 1.4 | 16
[10 empty] | 02010114xxy0 | 95 | 480/0.5 | 1.6 | 18.2
[10 empty] | 02010115xxy0 | 120 | 608/0.5 | 1.6 | 20.2
[10 empty] | 02010116xxy0 | 150 | 750/0.5 | 1.8 | 22.5
[10 empty] | 02010117xxy0 | 185 | 931/0.5 | 2 | 24.9
[10 empty] | 02010118xxy0 | 240 | 1200/0.5 | 2.2 | 28.4
[10 empty] | 02010119xxy0 | 300 | 1500/0.5 | 2.4 | 31
https://www.rrkabel.com/single-core/single-core-h05v | H05V-K & H07V-K | ['https://www.rrkabel.com/Uploads/Products/22/ProductZoomForMoreDetailsImage/02.jpg', 'https://www.rrkabel.com/Uploads/Products/22/ProductZoomImage/03.jpg', 'https://www.rrkabel.com/Uploads/Products/447/ProductFeaturesDetails/01.png', 'https://www.rrkabel.com/Uploads/Products/447/ProductFeaturesDetails/01.png'] | ['Cable designed for internal wiring in switch control, relay and instrumentation panels of power switchgear and for purposes such asstationary, static appliances, internal connectors in rectifier equipment, motor starters and controllers.'] | [11 empty] | ['DIN EN 50525-2-31, VDE 0285-525-2-31, BS EN 50525-2-31.'] | ['H05V-K 0.5 to 1 mm² - 300 / 500V, H07V-K 1.5 to 240 mm² - 450 / 750V'] | ['-30°C to +70°C'] | ['Cable diameter ≤ 8 mm : 4 x outer diameter', 'Approx. diameter > 8 to 12 mm : 5 x outer diameter', 'Approx. diameter > 12 mm : 6 x outer diameter'] | ['Conductor Class 5 flexible plain / metal coated stranded according to EN 60228.Insulation PVC (Polyvinyl chloride) TI1 to BS EN 50363- 3.'] | ['PVC self-extinguishing and flame retardant according to EN 60332-1-2.']
[21 empty] | H05V-K | 02020101xx1c | 02020101xx1c | 0.5 | 0.5 | 0.6 | 0.6 | 2.1 | 2.1 | 2.5 | 2.5 | 9 | 9
[21 empty] | H05V-K | 02020102xx1c | 02020102xx1c | 0.75 | 0.75 | 0.6 | 0.6 | 2.2 | 2.2 | 2.7 | 2.7 | 12 | 12
[21 empty] | H05V-K | 02020103xx1c | 02020103xx1c | 1 | 1 | 0.6 | 0.6 | 2.4 | 2.4 | 2.8 | 2.8 | 15 | 15
[21 empty] | H07V-K | 02020104xx1c | 02020104xx1c | 1.5 | 1.5 | 0.7 | 0.7 | 2.8 | 2.8 | 3.4 | 3.4 | 21 | 21
[21 empty] | H07V-K | 02020105xx1c | 02020105xx1c | 2.5 | 2.5 | 0.8 | 0.8 | 3.4 | 3.4 | 4.1 | 4.1 | 33 | 33
[21 empty] | H07V-K | 02020106xx1c | 02020106xx1c | 4 | 4 | 0.8 | 0.8 | 3.9 | 3.9 | 4.8 | 4.8 | 47 | 47
[21 empty] | H07V-K | 02020107xx1c | 02020107xx1c | 6 | 6 | 0.8 | 0.8 | 4.4 | 4.4 | 5.3 | 5.3 | 66 | 66
[21 empty] | H07V-K | 02020108xx1c | 02020108xx1c | 10 | 10 | 1 | 1 | 5.7 | 5.7 | 6.8 | 6.8 | 112 | 112
[21 empty] | H07V-K | 02020109xx1c | 02020109xx1c | 16 | 16 | 1 | 1 | 6.7 | 6.7 | 8.1 | 8.1 | 170 | 170
[21 empty] | H07V-K | 02020110xx1c | 02020110xx1c | 25 | 25 | 1.2 | 1.2 | 8.4 | 8.4 | 10.2 | 10.2 | 261 | 261
[21 empty] | H07V-K | 02020110xx1c | 02020110xx1c | 25 | 25 | 1.2 | 1.2 | 8.4 | 8.4 | 10.2 | 10.2 | 261 | 261
[21 empty] | H07V-K | 02020111xx1c | 02020111xx1c | 35 | 35 | 1.2 | 1.2 | 9.7 | 9.7 | 11.7 | 11.7 | 358 | 358
[21 empty] | H07V-K | 02020112xx1c | 02020112xx1c | 50 | 50 | 1.4 | 1.4 | 11.5 | 11.5 | 13.9 | 13.9 | 510 | 510
[21 empty] | H07V-K | 02020113xx1c | 02020113xx1c | 70 | 70 | 1.4 | 1.4 | 13.2 | 13.2 | 16 | 16 | 927 | 927
[21 empty] | H07V-K | 02020114xx1c | 02020114xx1c | 95 | 95 | 1.6 | 1.6 | 15.1 | 15.1 | 18.2 | 18.2 | 510 | 510
[21 empty] | H07V-K | 02020115xx1c | 02020115xx1c | 120 | 120 | 1.6 | 1.6 | 16.7 | 16.7 | 20.2 | 20.2 | 1170 | 1170
[21 empty] | H07V-K | 02020116xx1c | 02020116xx1c | 150 | 150 | 1.8 | 1.8 | 18.6 | 18.6 | 22.5 | 22.5 | 1459 | 1459
[21 empty] | H07V-K | 02020117xx1c | 02020117xx1c | 185 | 185 | 2 | 2 | 20.6 | 20.6 | 24.9 | 24.9 | 1776 | 1776
[21 empty] | H07V-K | 02020118xx1c | 02020118xx1c | 240 | 240 | 2.2 | 2.2 | 23.5 | 23.5 | 28.4 | 28.4 | 2333 | 2333
https://www.rrkabel.com/single-core/single-core-h05v2 | H05V2-K & H07V2-K | ['https://www.rrkabel.com/Uploads/Products/23/ProductZoomForMoreDetailsImage/02.jpg', 'https://www.rrkabel.com/Uploads/Products/23/ProductZoomImage/03.jpg', 'https://www.rrkabel.com/Uploads/Products/67/ProductFeaturesDetails/01.png', 'https://www.rrkabel.com/Uploads/Products/67/ProductFeaturesDetails/01.png'] | ['Heat resistant cable designed for internal wiring in switch control, relay and instrumentation panels of power switchgear and for purposes such as internal connectors in rectifier equipment, motor starters and controllers.'] | [11 empty] | ['BS/VDE EN 50525-2-31.'] | [] |  |  | ['Conductor Class 5 flexible plain / metal coated stranded according to EN 60228.Insulation PVC (Polyvinyl Chloride) TI3 to BS EN 50363 - 3.'] | ['PVC self-extinguishing and flame retardant according to EN 60332-1-2.']
[21 empty] | H05V2-K | 02030101xx3c | 02030101xx3c | 0.5 | 0.5 | 0.6 | 0.6 | 2.1 | 2.1 | 2.5 | 2.5 | 8.5 | 8.5
[21 empty] | H05V2-K | 02030102xx3c | 02030102xx3c | 0.75 | 0.75 | 0.6 | 0.6 | 2.2 | 2.2 | 2.7 | 2.7 | 11.5 | 11.5
[21 empty] | H05V2-K | 02030103xx3c | 02030103xx3c | 1 | 1 | 0.6 | 0.6 | 2.4 | 2.4 | 2.8 | 2.8 | 13.5 | 13.5
[21 empty] | H07V2-K | 02030104xx3c | 02030104xx3c | 1.5 | 1.5 | 0.7 | 0.7 | 2.8 | 2.8 | 3.4 | 3.4 | 20 | 20
[21 empty] | H07V2-K | 02030105xx3c | 02030105xx3c | 2.5 | 2.5 | 0.8 | 0.8 | 3.4 | 3.4 | 4.1 | 4.1 | 32 | 32
[21 empty] | H07V2-K | 02030106xx3c | 02030106xx3c | 4 | 4 | 0.8 | 0.8 | 3.9 | 3.9 | 4.8 | 4.8 | 46 | 46
[21 empty] | H07V2-K | 02030107xx3c | 02030107xx3c | 6 | 6 | 0.8 | 0.8 | 4.4 | 4.4 | 5.3 | 5.3 | 65 | 65
[21 empty] | H07V2-K | 02030108xx3c | 02030108xx3c | 10 | 10 | 1 | 1 | 5.7 | 5.7 | 6.8 | 6.8 | 110 | 110
[21 empty] | H07V2-K | 02030109xx3c | 02030109xx3c | 16 | 16 | 1 | 1 | 6.7 | 6.7 | 8.1 | 8.1 | 167 | 167
[21 empty] | H07V2-K | 02030110xx3c | 02030110xx3c | 25 | 25 | 1.2 | 1.2 | 8.4 | 8.4 | 10.2 | 10.2 | 257 | 257
[21 empty] | H07V2-K | 02030111xx3c | 02030111xx3c | 35 | 35 | 1.2 | 1.2 | 9.7 | 9.7 | 11.7 | 11.7 | 358 | 358
H07V2-K
H07V2-K
https://www.rrkabel.com/single-core/single-core-h05z | H05Z-K & H07Z-K | ['https://www.rrkabel.com/Uploads/Products/24/ProductZoomForMoreDetailsImage/02.jpg', 'https://www.rrkabel.com/Uploads/Products/24/ProductZoomImage/03.png', 'https://www.rrkabel.com/Uploads/Products/70/ProductFeaturesDetails/01.png', 'https://www.rrkabel.com/Uploads/Products/70/ProductFeaturesDetails/01.png'] | ['Halogen-free single-core wires are used for installation in dry environments for wiring up lighting fixtures and units where valuable assets are to be protected from further damage resulting from fire. These cables may be installed on, in and beneath plaster, as well as in closed installation ducts. The direct operating voltages is permitted up to 900 V against ground when they are used in rail-coaches. For the inner wiring of switch boards and distributors these are to be used with an alternating nominal voltage up to 1000V or a direct voltage up to 750V against ground.'] | [11 empty] | ['BS EN 50525-3-41.'] |  | ['-15°C to +90°C'] | ['Cable diameter ≤ 8 mm : 4 x outer diameter', 'Approx. diameter > 8 to 12 mm : 5 x outer diameter', 'Approx. diameter > 12 mm : 6 x outer diameter'] | [15 empty] | ['H05Z-K U / U 300 / 500V, H07Z-K U / U 450 / 750V O O'] | ['0.5 mmsquare to 1 mmsquare - H05Z-K, 1.5 mmsquare to 240 mmsquare - H07Z-K'] | ['Conductor Class 5 flexible plain/metal coated stranded according to EN 60228.Insulation Polyolefin cross linked EI5 to EN 50363-5.'] | ['Smoke density to acc. to EN 61034-2.Halogen free acc. to EN 50525-1, EN 60754-1.Corrosivity acc. to EN 60754-2Ozone resistant according to EN 60811-2-1.Self-extinguishing and flame retardant according to EN 60332-1-2.LSOH = Low Smoke Zero Halogen-Free.']
[21 empty] | H05Z-K | 02040101xx6c | 02040101xx6c |  |  | 0.6 | 0.6 | 1.9 | 1.9 | 2.4 | 2.4 | 9 | 9 |  |  |  |  | 0.5 | 0.5
[21 empty] | H05Z-K | 02040102xx6c | 02040102xx6c |  |  | 0.6 | 0.6 | 2.1 | 2.1 | 2.6 | 2.6 | 12 | 12 |  |  |  |  | 0.75 | 0.75
[21 empty] | H05Z-K | 02040103xx6c | 02040103xx6c |  |  | 0.6 | 0.6 | 2.1 | 2.1 | 2.8 | 2.8 | 15 | 15 |  |  |  |  | 1 | 1
[21 empty] | H07Z-K | 02040104xx6c | 02040104xx6c |  |  | 0.7 | 0.7 | 2.8 | 2.8 | 3.5 | 3.5 | 21 | 21 |  |  |  |  | 1.5 | 1.5
[21 empty] | H07Z-K | 02040105xx6c | 02040105xx6c |  |  | 0.8 | 0.8 | 3.4 | 3.4 | 4.3 | 4.3 | 33 | 33 |  |  |  |  | 2.5 | 2.5
[21 empty] | H07Z-K | 02040106xx6c | 02040106xx6c |  |  | 0.8 | 0.8 | 3.9 | 3.9 | 4.9 | 4.9 | 47 | 47 |  |  |  |  | 4 | 4
[21 empty] | H07Z-K | 02040107xx6c | 02040107xx6c |  |  | 0.8 | 0.8 | 4.4 | 4.4 | 5.5 | 5.5 | 66 | 66 |  |  |  |  | 6 | 6
[21 empty] | H07Z-K | 02040108xx6c | 02040108xx6c |  |  | 1 | 1 | 5.7 | 5.7 | 7.1 | 7.1 | 112 | 112 |  |  |  |  | 10 | 10
[21 empty] | H07Z-K | 02040109xx6c | 02040109xx6c |  |  | 1 | 1 | 6.7 | 6.7 | 8.4 | 8.4 | 169 | 169 |  |  |  |  | 16 | 16
[21 empty] | H07Z-K | 02040110xx6c | 02040110xx6c |  |  | 1.2 | 1.2 | 8.4 | 8.4 | 10.6 | 10.6 | 260 | 260 |  |  |  |  | 25 | 25
[21 empty] | H07Z-K | 02040111xx6c | 02040111xx6c |  |  | 1.2 | 1.2 | 9.7 | 9.7 | 12.1 | 12.1 | 358 | 358 |  |  |  |  | 35 | 35
[21 empty] | H07Z-K | 02040112xx6c | 02040112xx6c |  |  | 1.4 | 1.4 | 11.5 | 11.5 | 14.4 | 14.4 | 509 | 509 |  |  |  |  | 50 | 50
[21 empty] | H07Z-K | 02040113xx6c | 02040113xx6c |  |  | 1.4 | 1.4 | 13.2 | 13.2 | 16.61 | 16.61 | 701 | 701 |  |  |  |  | 70 | 70
[21 empty] | H07Z-K | 02040114xx6c | 02040114xx6c |  |  | 1.6 | 1.6 | 15.1 | 15.1 | 18.8 | 18.8 | 925 | 925 |  |  |  |  | 95 | 95
[21 empty] | H07Z-K | 02040115xx6c | 02040115xx6c |  |  | 1.6 | 1.6 | 16.7 | 16.7 | 20.9 | 20.9 | 1168 | 1168 |  |  |  |  | 120 | 120
[21 empty] | H07Z-K | 02040116xx6c | 02040116xx6c |  |  | 1.8 | 1.8 | 18.6 | 18.6 | 23.3 | 23.3 | 1456 | 1456 |  |  |  |  | 150 | 150
[21 empty] | H07Z-K | 02040117xx6c | 02040117xx6c |  |  | 2 | 2 | 20.6 | 20.6 | 25.8 | 25.8 | 1773 | 1773 |  |  |  |  | 185 | 185
[21 empty] | H07Z-K | 02040118xx6c | 02040118xx6c |  |  | 2.2 | 2.2 | 23.5 | 23.5 | 29.4 | 29.4 | 2329 | 2329 |  |  |  |  | 240 | 240
https://www.rrkabel.com/single-core/single-core-h05z1 | H05Z1-K & H07Z1-K | ['https://www.rrkabel.com/Uploads/Products/25/ProductZoomForMoreDetailsImage/02.jpg', 'https://www.rrkabel.com/Uploads/Products/25/ProductZoomImage/03.jpg', 'https://www.rrkabel.com/Uploads/Products/73/ProductFeaturesDetails/01.png', 'https://www.rrkabel.com/Uploads/Products/73/ProductFeaturesDetails/01.png'] | ['Halogen-free single-core wires are used for installation in dry environments for wiring up lighting fixtures and units where valuable assets are to protected from further damage resulting from fire. These cables may be installed on, in and beneath plaster, as well as in closed installation ducts. For use in public places such as: hospitals, schools, museums, airports, bus terminals, shops in general, etc., as well as in computer rooms, offices, production plants, switchboard wiring, laboratories, etc.'] | [11 empty] | ['BS EN 50525-3-31.'] |  | ['-30°C to +70°C'] | [] |  | ['Smoke density to acc. to EN 61034-2. Halogen free acc. to EN 50525-1, EN 60754-1. Corrosivity acc. to EN 60754-2.Ozone resistant according to EN 60811-2-1 or HD 505.2.1.Self-extinguishing and flame retardant according to EN 60332-1-2. LSOH = Low Smoke Zero Halogen.'] | [13 empty] | ['H05Z1- K UO / U 300 / 500V; H07Z1- K UO / U 450 / 750V'] | ['0.5 mmsquare to 1 mmsquare - H05Z1- K, 1.5 mmsquare to 240 mmsquare - H07Z1- K'] | ['Conductor Class 5 flexible plain / metal coated stranded according to EN 60228. Insulation of thermoplastic halogen-free compound type TI7 to EN 50363-7.'] |  |  |  | ['4 x outer diameter Approx. diameter > 8 to 12 mm: 5 x outer diameter Approx. diameter > 12 mm: 6 x outer diameter']
[21 empty] | H05Z1-K | 02050101xx7c | 02050101xx7c | 0.5 | 0.5 | 0.6 | 0.6 | 2.1 | 2.1 | 2.5 | 2.5 | 9.5 | 9.5
[21 empty] | H05Z1-K | 02050102xx7c | 02050102xx7c | 0.75 | 0.75 | 0.6 | 0.6 | 2.2 | 2.2 | 2.7 | 2.7 | 12.5 | 12.5
[21 empty] | H05Z1-K | 02050103xx7c | 02050103xx7c | 1 | 1 | 0.6 | 0.6 | 2.4 | 2.4 | 2.8 | 2.8 | 15.5 | 15.5
[21 empty] | H07Z1-K | 02050104xx7c | 02050104xx7c | 1.5 | 1.5 | 0.7 | 0.7 | 2.8 | 2.8 | 3.4 | 3.4 | 21.5 | 21.5
[21 empty] | H07Z1-K | 02050105xx7c | 02050105xx7c | 2.5 | 2.5 | 0.8 | 0.8 | 3.4 | 3.4 | 4.1 | 4.1 | 33.5 | 33.5
[21 empty] | H07Z1-K | 02050106xx7c | 02050106xx7c | 4 | 4 | 0.8 | 0.8 | 3.9 | 3.9 | 4.8 | 4.8 | 48 | 48
[21 empty] | H07Z1-K | 02050107xx7c | 02050107xx7c | 6 | 6 | 0.8 | 0.8 | 4.4 | 4.4 | 5.3 | 5.3 | 67 | 67
[21 empty] | H07Z1-K | 02050108xx7c | 02050108xx7c | 10 | 10 | 1 | 1 | 5.7 | 5.7 | 6.8 | 6.8 | 113 | 113
[21 empty] | H07Z1-K | 02050109xx7c | 02050109xx7c | 16 | 16 | 1 | 1 | 6.7 | 6.7 | 8.1 | 8.1 | 171 | 171
[21 empty] | H07Z1-K | 02050110xx7c | 02050110xx7c | 25 | 25 | 1.2 | 1.2 | 8.4 | 8.4 | 10.2 | 10.2 | 262 | 262
[21 empty] | H07Z1-K | 02040111xx6c | 02040111xx6c | 35 | 35 | 1.2 | 1.2 | 9.7 | 9.7 | 11.7 | 11.7 | 360 | 360
[21 empty] | H07Z1-K | 02050112xx7c | 02050112xx7c | 50 | 50 | 1.4 | 1.4 | 11.5 | 11.5 | 13.9 | 13.9 | 513 | 513
[21 empty] | H07Z1-K | 02050113xx7c | 02050113xx7c | 70 | 70 | 1.4 | 1.4 | 13.2 | 13.2 | 16 | 16 | 705 | 705
[21 empty] | H07Z1-K | 02050114xx7c | 02050114xx7c | 95 | 95 | 1.6 | 1.6 | 15.1 | 15.1 | 18.2 | 18.2 | 931 | 931
[21 empty] | H07Z1-K | 02050115xx7c | 02050115xx7c | 120 | 120 | 1.6 | 1.6 | 16.7 | 16.7 | 20.2 | 20.2 | 1175 | 1175
[21 empty] | H07Z1-K | 02050116xx7c | 02050116xx7c | 150 | 150 | 1.8 | 1.8 | 18.6 | 18.6 | 22.5 | 22.5 | 1264 | 1264
[21 empty] | H07Z1-K | 02050117xx7c | 02050117xx7c | 185 | 185 | 2 | 2 | 20.6 | 20.6 | 24.9 | 24.9 | 1783 | 1783
[21 empty] | H07Z1-K | 02050118xx7c | 02050118xx7c | 240 | 240 | 2.2 | 2.2 | 23.5 | 23.5 | 28.4 | 28.4 | 2341 | 2341
https://www.rrkabel.com/single-core/single-core-bs-6231 | BS 6231 CK 90°C | ['https://www.rrkabel.com/Uploads/Products/26/ProductZoomForMoreDetailsImage/02.jpg', 'https://www.rrkabel.com/Uploads/Products/26/ProductZoomImage/03.jpg', 'https://www.rrkabel.com/Uploads/Products/76/ProductFeaturesDetails/01.png', 'https://www.rrkabel.com/Uploads/Products/76/ProductFeaturesDetails/01.png'] | ['High temperature, flame retardant cable designed for use in switch control, relay and instrumentation panels of power switchgear and for purposes such as internal connectors in rectifier equipment, motor starters and controllers.'] | [11 empty] | ['BS6231 Type CK.'] | ['600 / 1000V'] |  | ['Cable diameter ≤ 8 mm : 4 x outer diameter.', 'Approx. diameter > 8 to 12 mm: 5 x outer diameter.', 'Approx. diameter > 12 mm: 6 x outer diameter.'] |  | ['PVC self-extinguishing and flame retardant according to EN 60332-1-2.'] | [20 empty] | ['90°C (105°C for 15,000 hours)']
[21 empty] | 02060101xx3c | 02060101xx3c |  |  |  | 0.8 | 0.8 | 2.4 | 2.4 | 3 | 3 | 11 | 11 |  |  |  |  | 0.5 | 0.5
[21 empty] | 02060102xx3c | 02060102xx3c |  |  |  | 0.8 | 0.8 | 2.6 | 2.6 | 3.1 | 3.1 | 14 | 14 |  |  |  |  | 0.75 | 0.75
[21 empty] | 02060103xx3c | 02060103xx3c |  |  |  | 0.8 | 0.8 | 2.7 | 2.7 | 3.3 | 3.3 | 16 | 16 |  |  |  |  | 1 | 1
[21 empty] | 02060104xx3c | 02060104xx3c |  |  |  | 0.8 | 0.8 | 3 | 3 | 3.6 | 3.6 | 21 | 21 |  |  |  |  | 1.5 | 1.5
[21 empty] | 02060105xx3c | 02060105xx3c |  |  |  | 0.8 | 0.8 | 3.4 | 3.4 | 4.1 | 4.1 | 32 | 32 |  |  |  |  | 2.5 | 2.5
[21 empty] | 02060106xx3c | 02060106xx3c |  |  |  | 0.8 | 0.8 | 3.9 | 3.9 | 4.8 | 4.8 | 46 | 46 |  |  |  |  | 4 | 4
[21 empty] | 02060107xx3c | 02060107xx3c |  |  |  | 0.8 | 0.8 | 4.4 | 4.4 | 5.3 | 5.3 | 64 | 64 |  |  |  |  | 6 | 6
[21 empty] | 02060108xx3c | 02060108xx3c |  |  |  | 1 | 1 | 5.7 | 5.7 | 7.2 | 7.2 | 109 | 109 |  |  |  |  | 10 | 10
[21 empty] | 02060109xx3c | 02060109xx3c |  |  |  | 1 | 1 | 6.7 | 6.7 | 9 | 9 | 166 | 166 |  |  |  |  | 16 | 16
[21 empty] | 02060110xx3c | 02060110xx3c |  |  |  | 1.2 | 1.2 | 8.4 | 8.4 | 11.5 | 11.5 | 256 | 256 |  |  |  |  | 25 | 25
[21 empty] | 02060111xx3c | 02060111xx3c |  |  |  | 1.2 | 1.2 | 9.7 | 9.7 | 12.5 | 12.5 | 352 | 352 |  |  |  |  | 35 | 35
[21 empty] | 02060112xx3c | 02060112xx3c |  |  |  | 1.4 | 1.4 | 11.5 | 11.5 | 15.4 | 15.4 | 501 | 501 |  |  |  |  | 50 | 50
[21 empty] | 02060113xx3c | 02060113xx3c |  |  |  | 1.4 | 1.4 | 13.2 | 13.2 | 17.5 | 17.5 | 692 | 692 |  |  |  |  | 70 | 70
[21 empty] | 02060114xx3c | 02060114xx3c |  |  |  | 1.6 | 1.6 | 15.1 | 15.1 | 19.2 | 19.2 | 914 | 914 |  |  |  |  | 95 | 95
[21 empty] | 02060115xx3c | 02060115xx3c |  |  |  | 1.6 | 1.6 | 16.7 | 16.7 | 21.2 | 21.2 | 1155 | 1155 |  |  |  |  | 120 | 120
[21 empty] | 02060116xx3c | 02060116xx3c |  |  |  | 1.8 | 1.8 | 18.6 | 18.6 | 23.9 | 23.9 | 1441 | 1441 |  |  |  |  | 150 | 150
[21 empty] | 02060117xx3c | 02060117xx3c |  |  |  | 2 | 2 | 20.6 | 20.6 | 25.9 | 25.9 | 1754 | 1754 |  |  |  |  | 185 | 185
[21 empty] | 02060118xx3c | 02060118xx3c |  |  |  | 2.2 | 2.2 | 23.5 | 23.5 | 28.9 | 28.9 | 2305 | 2305 |  |  |  |  | 240 | 240